## GHG acct
Greenhouse Gas Accounting for CHP Project
UM Heating Plant Before and After CHP Project on-line
Actual to Projected Emissions Comparison, Firing Natural Gas
|  |  | EPA Emissions Hub for Non-Baseload NWPP GHG EF: | 0.73843 | MTCO2e/MWh
GHG Source Base Year: 2018 | Actual Natural Gas Heat Input MMBtu/year | GHG Scope 1 Emissions: Combustion Mt/year CO2e(4) | NWE Power Purchased MWh | GHG Scope 2 Emissions: Power Purchase Mt/year CO2e(5) | UM Power Produced MWh | GHG Emissions: Total Mt/year CO2e
Boiler #1 | 197494.2925 | 10489.8698
Boiler #2 | 47527 | 2524.3871
Boiler #3 | 6743.7075 | 358.1907
Power Purchase - NWE (1) |  |  | 36080.4436 | 26642.825
Total Base Year | 251765 | 13372.4476 | 36080.4436 | 26642.825 |  | 40015.2726
CHP Project On-Line(2)
Combustion Gas Turbine | 431900.0919 | 22940.287 |  |  | 24422.2286
Steam Turbine |  |  |  |  | 7087.1869
HRSG Duct Burner | 21889.5096 | 1162.6569
Boiler #1(3) | 0
Boiler #2(3) | 0
Power Purchase - NWE (1) |  |  | 5461.5333 | 4032.9514
Total CHP On-Line | 453789.6014 | 24102.9439 | 5461.5333 | 4032.9514 | 31509.4155 | 28135.8953
[5 empty] | Total Projected GHG Emissions Reduction: | 11879.3773
[5 empty] | Savings in GHG Emissions | 29.69%
(1) NWE Power Purchase, includes transmission losses estimated at 5.1 % of load - per EPA eGRID 2019 Grid Gross Loss
for western US. | Link here
(2) Projected annual operating levels
(3) CHP plant is capable of 70,000 lbs/hr of steam production with duct burner. During the base year of 2018, there
were no hours in the year that exceeded 70,000 lbs/hr, so there wouldappear to be no need to engage either
of the existing heating plant boilers. Maximum steam usage was 63,240 lbs/hr.
(4) GHG Emissions Factors from 40 CFR 98, Subpart C: Table C-1 & C-2, GWP from Subpart A: Table A-1
(5)Apply 2019 eGRID GHG Emissions Factor for NWPP Region, Non-Baseload per recommendation of US DOE Northwest
Combined Heat and Power Technical Assistance Partnership (NW CHP TAP)
Scope 1 Emission Factor:
40 CFR Appendix Table C-1 to Subpart C |  |  | GWP | Emission Factors
Natural Gas Default CO2 Emission Factor | 53.06 | kgCO2/MMBtu | 1 | 53.06 | kgCO2e/MMBtu
Natural Gas Default CH4 Emission Factor | 0.001 | kg CH4/MMBtu | 25 | 0.025 | kgCO2e/MMBtu
Natural Gas Default N2O Emission Factor | 0.0001 | kg N2O/MMBtu | 298 | 0.0298 | kgCO2e/MMBtu
|  |  | Total: | 53.1148 | kgCO2e/MMBtu
|  |  |  | 0.053115 | MTCO2e/MMBtu
Scope 2 Emission Factor:
Non-Baseload EF from EPA eGRID NWPP Region:
| lb/MWh | MT/MWh | GWP | Emission Factors
CO2 | 1617.5 | 0.73369 | 1 | 0.73369 | MTCO2e/MWh
CH4 | 0.156 | 7.076e-05 | 25 | 0.001769 | MTCO2e/MWh
N2O | 0.022 | 9.979e-06 | 298 | 0.0029738 | MTCO2e/MWh
|  |  | Total: | 0.73843 | MTCO2e/MWh
| 1 metric ton = | 2204.6226 | lbs
STARS Program Calculations, OP2
| Square Footage of Campus Served | GHG Emissions: Total Mt/year CO2e | GHG Emissions: kg/year CO2e | GHG Emissions per Square Foot
2018 Actual | 3269529 | 40016 | 40016000 | 12.2391
Under the Proposed CHP Project | 3499740 | 28136 | 28136000 | 8.0395
|  |  | Benchmark Reduction: | 4.1996
|  |  | Percentage Reduction: | 34.31%
Note on A8: Kerns, Brian P.: From Utility Rate Analyses for CHPV6 sum(s5:w5) (May - Sep)
Note on A9: Kerns, Brian P.: Estimated: 1 week/yr during winter (Oct-Apr): 7days/212days=3.3%
Note on D10: Kerns, Brian P.: From Utility Rate Analyses for CHPV6, sum(ac62Lan62) for jan-dec 2018
Note on B11: Kerns, Brian P.: Utility Rate Analyses for CHPV6, sum(p5:aa5)
Note on B14: Kerns, Brian P.: Power Engineers - UM Steam and Power Analysis - DVH CHKS and ADDS-2-check - L7
Note on F14: Kerns, Brian P.: Power Engineers - UM Steam and Power Analysis - DVH CHKS and ADDS-2-check - S10
Note on B16: Kerns, Brian P.: Power Engineers - UM Steam and Power Analysis - DVH CHKS and ADDS-2-check - M12
Note on D19: Kerns, Brian P.: Power Engineers - UM Steam and Power Analysis - DVH CHKS and ADDS-2-check - N12

## eGRID Table
Screen shot of EPA Emissions Hub captured 5/6/2021
link here