University of Montana - Facilities Condition Inventory	Priorities	1
	Deficiency Detail by Building	2
	Site:	UM Missoula Main Campus	Area Correction:	1.44	Last Audit Date:	1/11/2007	3
	4
	Building:	1000 East Beckwith	Gross Area:	2,016	Sq Ft	Report Renewal Cost:	$105,364	5
	Category:	11B	Cost/Sq Ft:	$284.21	Deficiency Ratio:	18.4%	6
	Const. Date:	1970	Replacement Cost:	$572,988	7
	Comp.	System
	Entry #	Initial	Last	Unit	Renew	Replace
	Component	Entry	Update	Pri	%	Cost	Cost	Cost	Description
System:	Foundations (1)	Totals:	$220	$16,572
	795	Exterior Steps/Retaining Walls (B)	04-28-2005	01-11-2007	2	10%	$1.09	$220	Back yd ret wall needs to rblt. Rear conc steps repair. Front 
	driveway/walkway aggregate is showing.
System:	Envelope (2)	Totals:	$42,477	$61,508
	926	Exterior Walls (A)	01-11-2007	01-11-2007	2	100%	$21.07	$42,477	Exterior walls, trim and walk need painting
System:	Roof System (4)	Totals:	$6,259	$10,644
	796	Covering (B)	04-28-2005	04-28-2005	2	100%	$2.45	$4,939	ROOF IS AT END OF USEFULL LIFE AND FAILS OCCASIONALLY.
	797	Insulation (C)	04-28-2005	04-28-2005	5	50%	$1.31	$1,320	ADD ADDITIONAL ROOF INSULATION.
System:	Finishes (5)	Totals:	$5,358	$95,276
	800	Floor Finishes (D)	04-28-2005	04-28-2005	2	25%	$10.63	$5,358	Living room still needs new carpet.
System:	HVAC System (7)	Totals:	$20,941	$62,133
	935	Heating (A)	01-11-2007	01-11-2007	2	75%	$13.85	$20,941	Ductwork, heat levels need work. Furnace unable to keep all floors the 
	same temperature.
System:	Plumbing System (8)	Totals:	$5,897	$58,968
	937	Fixtures (A)	01-11-2007	01-11-2007	2	10%	$9.69	$1,954	faucets need to be replaced
	938	Supply Piping (B)	01-11-2007	01-11-2007	2	10%	$13.67	$2,756	piping is beginning to show wear.
	939	Waste Piping (C)	01-11-2007	01-11-2007	2	10%	$5.89	$1,187	piping is getting near its expected life
	Deficiency Detail by Building	FCI Version:  1.1.0
	Priorities 1-6	5/12/2009
	Priorities 1-6	Page 1 of 71

	University of Montana - Facilities Condition Inventory	Priorities	1
	Deficiency Detail by Building	2
	Site:	UM Missoula Main Campus	Area Correction:	1.44	Last Audit Date:	1/11/2007	3
	4
	Building:	1000 East Beckwith	Gross Area:	2,016	Sq Ft	Report Renewal Cost:	$105,364	5
	Category:	11B	Cost/Sq Ft:	$284.21	Deficiency Ratio:	18.4%	6
	Const. Date:	1970	Replacement Cost:	$572,988	7
	Comp.	System
	Entry #	Initial	Last	Unit	Renew	Replace
	Component	Entry	Update	Pri	%	Cost	Cost	Cost	Description
System:	Electrical System (9)	Totals:	$24,212	$38,788
	801	Building Service (A)	04-28-2005	04-28-2005	4	100%	$5.21	$10,503	SERVICE TO BUILDING NEEDS TO BE RELOCATED AND 
	INCREASED TO HANDLE COMMERCIAL DEMAND.
	940	Distribution (C)	01-11-2007	01-11-2007	3	100%	$6.80	$13,709	old wiring needs to be replaced and upgraded to current code levels
	Deficiency Detail by Building	FCI Version:  1.1.0
	Priorities 1-6	5/12/2009
	Priorities 1-6	Page 2 of 71

	University of Montana - Facilities Condition Inventory	Priorities	1
	Deficiency Detail by Building	2
	Site:	UM Missoula Main Campus	Area Correction:	1.04	Last Audit Date:	9/24/2008	3
	4
	Building:	Art Annex/Grizzly Pool	Gross Area:	40,293	Sq Ft	Report Renewal Cost:	$2,038,471	5
	Category:	3A	Cost/Sq Ft:	$216.03	Deficiency Ratio:	23.4%	6
	Const. Date:	1955	Replacement Cost:	$8,704,497	7
	Comp.	System
	Entry #	Initial	Last	Unit	Renew	Replace
	Component	Entry	Update	Pri	%	Cost	Cost	Cost	Description
System:	Foundations (1)	Totals:	$38,560	$192,601
	252	Footings/Foundation Walls (A)	09-24-2008	04-28-2005	2	30%	$3.19	$38,560	Parking lot water drainage problem. South end of pool eroding due to 
	chlorine in water.
System:	Envelope (2)	Totals:	$77,564	$632,600
	253	Exterior Walls (A)	09-24-2008	04-28-2005	2	20%	$4.18	$33,685	Paint exterior of building.
	1018	Exterior Windows (B)	09-24-2008	09-24-2008	5	10%	$4.94	$19,905	W end. Window frames not sealed, big gaps.
	254	Exterior Doors/Hatches (C)	09-24-2008	04-28-2005	2	70%	$0.85	$23,974	Replace all damaged doors, especially roll-up door on S end.
System:	Roof System (4)	Totals:	$119,670	$232,491
	255	Structure (A)	09-24-2008	04-28-2005	2	100%	$1.66	$66,886	Repair roof structure.
	256	Insulation (C)	09-24-2008	04-28-2005	5	100%	$1.31	$52,784	Add additional attic insulation.
System:	Finishes (5)	Totals:	$770,463	$1,578,680
	257	Interior Walls (A)	09-24-2008	04-28-2005	2	100%	$10.92	$440,000	Repair leaking pool walls.
	1020	Ceilings (B)	09-24-2008	09-24-2008	2	15%	$8.23	$49,742	Several areas, especially in arts portion are in dire need of 
	repair/replacement.
	258	Interior Doors/Hardware/Windows (C)	09-24-2008	04-28-2005	3	50%	$6.48	$130,549	Install compliant hardware on the doors.  Bathrooms not ADA compliant.
	1021	Floor Finishes (D)	09-24-2008	09-24-2008	2	10%	$7.62	$30,703	Hallway and pool floor have several cracks.
	259	Wall Finishes (E)	09-24-2008	04-28-2005	2	50%	$5.93	$119,469	Paint the interior walls.
System:	Specialties (6)	Totals:	$179,808	$499,633
	260	Toilet Partitions (A)	04-28-2005	04-28-2005	2	25%	$1.51	$15,211	Replace toilet partitions.
	1023	Signage/Directories (B)	09-24-2008	09-24-2008	3	50%	$1.01	$20,348	Not Braille
	1024	Fixed Seating/Risers (C)	09-24-2008	09-24-2008	2	100%	$3.58	$144,249	Pool Balcony not ADA and serious signs of wear.
	Deficiency Detail by Building	FCI Version:  1.1.0
	Priorities 1-6	5/12/2009
	Priorities 1-6	Page 3 of 71

	University of Montana - Facilities Condition Inventory	Priorities	1
	Deficiency Detail by Building	2
	Site:	UM Missoula Main Campus	Area Correction:	1.04	Last Audit Date:	9/24/2008	3
	4
	Building:	Art Annex/Grizzly Pool	Gross Area:	40,293	Sq Ft	Report Renewal Cost:	$2,038,471	5
	Category:	3A	Cost/Sq Ft:	$216.03	Deficiency Ratio:	23.4%	6
	Const. Date:	1955	Replacement Cost:	$8,704,497	7
	Comp.	System
	Entry #	Initial	Last	Unit	Renew	Replace
	Component	Entry	Update	Pri	%	Cost	Cost	Cost	Description
System:	HVAC System (7)	Totals:	$199,853	$814,322
	263	Heating (A)	09-24-2008	04-28-2005	2	50%	$8.82	$177,692	Replace heating equipment in annex side, plus pool side.
	1026	Ventilating (B)	09-24-2008	09-24-2008	1	50%	$1.10	$22,161	South Side of annex has poor to no ventilating. Serious situation considering 
	flamable liquids and high heat units and health of occupants.
System:	Plumbing System (8)	Totals:	$216,978	$769,596
	264	Fixtures (A)	09-24-2008	04-28-2005	2	15%	$6.50	$39,286	Replace plumbing fixtures. 
	265	Supply Piping (B)	09-24-2008	04-28-2005	2	35%	$7.37	$103,936	Replace the supply piping system. 
	266	Waste Piping (C)	09-24-2008	04-28-2005	2	35%	$5.23	$73,756	Replace  the waste piping system., mechanical rebuild.
System:	Electrical System (9)	Totals:	$334,649	$1,076,226
	267	Building Service (A)	04-28-2005	04-28-2005	2	3%	$6.98	$8,437	Replace meters. 
	268	Lighting (B)	09-24-2008	04-28-2005	2	80%	$6.28	$202,432	Replace lighting with T8 lamps and electronic ballasts. 
	269	Distribution (C)	09-24-2008	04-28-2005	2	40%	$7.68	$123,780	Remove/replace secondary panels. 
System:	Safety System (11)	Totals:	$100,926	$480,695
	270	Exit/Emergency Lighting/Alarms (C)	04-28-2005	04-28-2005	3	12%	$4.04	$19,534	Replace exit/emergency/alarm systems. 
	1028	Exit/Emergency Lighting/Alarms (C)	09-24-2008	09-24-2008	3	50%	$4.04	$81,392	emergency lighting poor, alarms out.
	Deficiency Detail by Building	FCI Version:  1.1.0
	Priorities 1-6	5/12/2009
	Priorities 1-6	Page 4 of 71

	University of Montana - Facilities Condition Inventory	Priorities	1
	Deficiency Detail by Building	2
	Site:	UM Missoula Main Campus	Area Correction:	1.08	Last Audit Date:	4/28/2005	3
	4
	Building:	Brantly Hall	Gross Area:	38,935	Sq Ft	Report Renewal Cost:	$1,124,318	5
	Category:	3A	Cost/Sq Ft:	$224.34	Deficiency Ratio:	12.9%	6
	Const. Date:	1923	Replacement Cost:	$8,734,678	7
	Comp.	System
	Entry #	Initial	Last	Unit	Renew	Replace
	Component	Entry	Update	Pri	%	Cost	Cost	Cost	Description
System:	Foundations (1)	Totals:	$128,875	$193,507
	197	Footings/Foundation Walls (A)	04-28-2005	04-28-2005	2	50%	$3.32	$64,632	Repair foundation. 
	198	Exterior Steps/Retaining Walls (B)	04-28-2005	04-28-2005	2	100%	$1.65	$64,243	Replace steps/walls. 
System:	Envelope (2)	Totals:	$144,488	$635,030
	199	Exterior Walls (A)	04-28-2005	04-28-2005	2	10%	$4.34	$16,898	Tuckpoint clean - seal. 
	200	Exterior Windows (B)	04-28-2005	04-28-2005	2	50%	$5.13	$99,868	Replace windows. 
	201	Exterior Doors/Hatches (C)	04-28-2005	04-28-2005	2	80%	$0.89	$27,722	Replace entry doors. 
System:	Floor System (3)	Totals:	$149,861	$788,434
	202	Floor Structure (A)	04-28-2005	04-28-2005	2	10%	$15.69	$61,089	Replace Basement Floor. 
	203	Stair Treads/Risers (B)	04-28-2005	04-28-2005	2	50%	$4.56	$88,772	Replace stairs. 
System:	Roof System (4)	Totals:	$166,253	$233,221
	204	Covering (B)	04-28-2005	04-28-2005	2	100%	$2.91	$113,301	Replace clay tile roof. 
	205	Insulation (C)	04-28-2005	04-28-2005	5	100%	$1.36	$52,952	Replace existing insulation with UBC compliant R factor insulation. 
System:	Finishes (5)	Totals:	$257,282	$1,583,876
	206	Interior Walls (A)	04-28-2005	04-28-2005	2	10%	$11.34	$44,152	Replace walls as needed. 
	207	Ceilings (B)	04-28-2005	04-28-2005	2	25%	$8.54	$83,126	Replace ceilings as needed. 
	208	Interior Doors/Hardware/Windows (C)	04-28-2005	04-28-2005	2	30%	$6.73	$78,610	Replace all doors, glazing and door handles. 
	209	Floor Finishes (D)	04-28-2005	04-28-2005	2	5%	$7.92	$15,418	Replace carpet & tile. 
	210	Wall Finishes (E)	04-28-2005	04-28-2005	2	15%	$6.16	$35,976	Complete patch & paint. 
	Deficiency Detail by Building	FCI Version:  1.1.0
	Priorities 1-6	5/12/2009
	Priorities 1-6	Page 5 of 71

	University of Montana - Facilities Condition Inventory	Priorities	1
	Deficiency Detail by Building	2
	Site:	UM Missoula Main Campus	Area Correction:	1.08	Last Audit Date:	4/28/2005	3
	4
	Building:	Brantly Hall	Gross Area:	38,935	Sq Ft	Report Renewal Cost:	$1,124,318	5
	Category:	3A	Cost/Sq Ft:	$224.34	Deficiency Ratio:	12.9%	6
	Const. Date:	1923	Replacement Cost:	$8,734,678	7
	Comp.	System
	Entry #	Initial	Last	Unit	Renew	Replace
	Component	Entry	Update	Pri	%	Cost	Cost	Cost	Description
System:	Specialties (6)	Totals:	$3,056	$501,093
	211	Toilet Partitions (A)	04-28-2005	04-28-2005	2	5%	$1.57	$3,056	R/R damaged and worn out toilet partitions.
System:	HVAC System (7)	Totals:	$71,329	$816,856
	212	Heating (A)	04-28-2005	04-28-2005	2	20%	$9.16	$71,329	New heating & install building automation system. 
System:	Plumbing System (8)	Totals:	$128,212	$772,470
	213	Fixtures (A)	04-28-2005	04-28-2005	2	10%	$6.75	$26,281	Replace worn out fixtures. 
	214	Supply Piping (B)	04-28-2005	04-28-2005	2	20%	$7.66	$59,648	Replace entire old and worn out system. 
	215	Waste Piping (C)	04-28-2005	04-28-2005	2	20%	$5.43	$42,283	Replace existing system with new gutters. 
System:	Electrical System (9)	Totals:	$56,701	$1,079,668
	216	Building Service (A)	04-28-2005	04-28-2005	2	1%	$7.25	$2,823	Replace old, inadequate system with new electrical meters. 
	217	Lighting (B)	04-28-2005	04-28-2005	2	9%	$6.52	$22,847	New lighting w/ electronic ballasts & T8 lamps. 
	218	Distribution (C)	04-28-2005	04-28-2005	2	10%	$7.97	$31,031	Worn out secondary panel, switches, outlets, receptacles .
System:	Safety System (11)	Totals:	$18,261	$482,405
	220	Exit/Emergency Lighting/Alarms (C)	04-28-2005	04-28-2005	2	10%	$4.19	$16,314	Replace old exit lights with new exit lights. 
	221	Asbestos/Hazardous Material (D)	04-28-2005	04-28-2005	3	20%	$0.25	$1,947	Remove remaining asbestos. 
	Deficiency Detail by Building	FCI Version:  1.1.0
	Priorities 1-6	5/12/2009
	Priorities 1-6	Page 6 of 71

	University of Montana - Facilities Condition Inventory	Priorities	1
	Deficiency Detail by Building	2
	Site:	UM Missoula Main Campus	Area Correction:	1.04	Last Audit Date:	6/20/2007	3
	4
	Building:	Chemistry/Pharmacy	Gross Area:	47,833	Sq Ft	Report Renewal Cost:	$449,526	5
	Category:	4A	Cost/Sq Ft:	$234.40	Deficiency Ratio:	4.0%	6
	Const. Date:	1938	Replacement Cost:	$11,212,055	7
	Comp.	System
	Entry #	Initial	Last	Unit	Renew	Replace
	Component	Entry	Update	Pri	%	Cost	Cost	Cost	Description
System:	Foundations (1)	Totals:	$49,938	$694,535
	965	Footings/Foundation Walls (A)	06-20-2007	06-20-2007	2	5%	$12.93	$30,924	Some spots are wearing out.
	966	Exterior Steps/Retaining Walls (B)	06-20-2007	06-20-2007	2	25%	$1.59	$19,014	Both are showing signs of repair.
System:	Envelope (2)	Totals:	$36,544	$908,827
	967	Exterior Walls (A)	06-20-2007	06-20-2007	2	10%	$7.64	$36,544	West end and sections of the north end are showing signs of wear.
System:	Roof System (4)	Totals:	$2,569	$457,283
	968	Covering (B)	06-20-2007	06-20-2007	2	1%	$5.37	$2,569	Minor attention needed.
System:	Finishes (5)	Totals:	$82,416	$2,151,050
	969	Interior Walls (A)	06-20-2007	06-20-2007	2	5%	$17.21	$41,160	Contractor left holes in walls.
	970	Ceilings (B)	06-20-2007	06-20-2007	2	5%	$8.23	$19,683	Tiles damaged or water stained.
	971	Floor Finishes (D)	06-20-2007	06-20-2007	2	5%	$9.02	$21,573	Areas starting to show signs of serious wear.
System:	Specialties (6)	Totals:	$7,247	$729,932
	972	Signage/Directories (B)	06-20-2007	06-20-2007	3	15%	$1.01	$7,247	Some room numbers are missing.
System:	Plumbing System (8)	Totals:	$267,028	$1,209,218
	973	Supply Piping (B)	06-20-2007	06-20-2007	2	35%	$8.63	$144,480	Old piping need to be updated
	974	Waste Piping (C)	06-20-2007	06-20-2007	2	35%	$7.32	$122,548	Old piping needs to be updated.
System:	Conveying (10)	Totals:	$2,210	$220,988
	975	Elevator/Lift (A)	06-20-2007	06-20-2007	3	1%	$4.62	$2,210	Floor slot needs attention.
	Deficiency Detail by Building	FCI Version:  1.1.0
	Priorities 1-6	5/12/2009
	Priorities 1-6	Page 7 of 71

	University of Montana - Facilities Condition Inventory	Priorities	1
	Deficiency Detail by Building	2
	Site:	UM Missoula Main Campus	Area Correction:	1.04	Last Audit Date:	6/20/2007	3
	4
	Building:	Chemistry/Pharmacy	Gross Area:	47,833	Sq Ft	Report Renewal Cost:	$449,526	5
	Category:	4A	Cost/Sq Ft:	$234.40	Deficiency Ratio:	4.0%	6
	Const. Date:	1938	Replacement Cost:	$11,212,055	7
	Comp.	System
	Entry #	Initial	Last	Unit	Renew	Replace
	Component	Entry	Update	Pri	%	Cost	Cost	Cost	Description
System:	Safety System (11)	Totals:	$1,574	$474,503
	976	Extinguishing System (B)	06-20-2007	06-20-2007	3	1%	$3.29	$1,574	Needs to be reviewed to make sure everything works.
	Deficiency Detail by Building	FCI Version:  1.1.0
	Priorities 1-6	5/12/2009
	Priorities 1-6	Page 8 of 71

	University of Montana - Facilities Condition Inventory	Priorities	1
	Deficiency Detail by Building	2
	Site:	UM Missoula Main Campus	Area Correction:	1.44	Last Audit Date:	4/28/2005	3
	4
	Building:	Clinical Psychology	Gross Area:	5,280	Sq Ft	Report Renewal Cost:	$109,994	5
	Category:	4C	Cost/Sq Ft:	$362.15	Deficiency Ratio:	5.8%	6
	Const. Date:	1983	Replacement Cost:	$1,912,152	7
	Comp.	System
	Entry #	Initial	Last	Unit	Renew	Replace
	Component	Entry	Update	Pri	%	Cost	Cost	Cost	Description
System:	Foundations (1)	Totals:	$9,451	$100,267
	272	Footings/Foundation Walls (A)	04-28-2005	04-28-2005	2	10%	$17.90	$9,451	Repair damage to front steps.
System:	Floor System (3)	Totals:	$16,051	$105,811
	273	Stair Treads/Risers (B)	04-28-2005	04-28-2005	3	50%	$6.08	$16,051	Bring stairs to basement to meet codes.
System:	Roof System (4)	Totals:	$52,536	$64,786
	274	Covering (B)	04-28-2005	04-28-2005	2	100%	$6.47	$34,162	Replace B.U. roof with hypalon.
	275	Insulation (C)	04-28-2005	04-28-2005	2	100%	$3.48	$18,374	Add more rigid insulation to the roof.
System:	Finishes (5)	Totals:	$23,829	$299,957
	277	Floor Finishes (D)	04-28-2005	04-28-2005	2	25%	$11.35	$14,982	Replace worn-out carpet.
	278	Wall Finishes (E)	04-28-2005	04-28-2005	2	15%	$11.17	$8,847	Worn out spots need paint, etc.
System:	Specialties (6)	Totals:	$2,305	$139,075
	279	Chalk/Tackboards/Cabinets (D)	04-28-2005	04-28-2005	3	5%	$8.73	$2,305	Replace old chalkboards with LCS boards.
System:	Electrical System (9)	Totals:	$5,822	$153,120
	281	Building Service (A)	04-28-2005	04-28-2005	3	2%	$4.03	$426	Install new meters.
	282	Lighting (B)	04-28-2005	04-28-2005	5	11%	$9.29	$5,396	Replace old fixtures with new T8 lamps and electronic ballasts.
	Deficiency Detail by Building	FCI Version:  1.1.0
	Priorities 1-6	5/12/2009
	Priorities 1-6	Page 9 of 71

	University of Montana - Facilities Condition Inventory	Priorities	1
	Deficiency Detail by Building	2
	Site:	UM Missoula Main Campus	Area Correction:	1.16	Last Audit Date:	4/28/2005	3
	4
	Building:	Corbin Hall	Gross Area:	23,190	Sq Ft	Report Renewal Cost:	$680,157	5
	Category:	3A	Cost/Sq Ft:	$240.96	Deficiency Ratio:	12.2%	6
	Const. Date:	1927	Replacement Cost:	$5,587,862	7
	Comp.	System
	Entry #	Initial	Last	Unit	Renew	Replace
	Component	Entry	Update	Pri	%	Cost	Cost	Cost	Description
System:	Foundations (1)	Totals:	$10,262	$123,835
	154	Exterior Steps/Retaining Walls (B)	04-28-2005	04-28-2005	2	25%	$1.77	$10,262	Step repair
System:	Envelope (2)	Totals:	$142,990	$406,289
	155	Exterior Walls (A)	04-28-2005	04-28-2005	2	10%	$4.66	$10,807	Clean Tuckpoint waterproof bricks
	156	Exterior Windows (B)	04-28-2005	04-28-2005	2	100%	$5.51	$127,777	Replace all windows.
	157	Exterior Doors/Hatches (C)	04-28-2005	04-28-2005	2	20%	$0.95	$4,406	Replace doors.
System:	Floor System (3)	Totals:	$44,757	$504,383
	158	Floor Structure (A)	04-28-2005	04-28-2005	2	10%	$16.85	$39,075	Replace wood basement floor.
	159	Stair Treads/Risers (B)	04-28-2005	04-28-2005	3	5%	$4.90	$5,682	replace stair treads code compliance
System:	Roof System (4)	Totals:	$106,210	$149,344
	160	Covering (B)	04-28-2005	04-28-2005	2	100%	$3.12	$72,353	Replace roof tile.
	161	Insulation (C)	04-28-2005	04-28-2005	5	100%	$1.46	$33,857	Add insulation.
System:	Finishes (5)	Totals:	$165,599	$1,013,403
	162	Interior Walls (A)	04-28-2005	04-28-2005	2	10%	$12.18	$28,245	Patch and repair interior walls.
	163	Ceilings (B)	04-28-2005	04-28-2005	2	10%	$9.18	$21,288	Patch and repair ceiling tiles.
	165	Floor Finishes (D)	04-28-2005	04-28-2005	2	20%	$8.50	$39,423	Replace and install new carpet.
	166	Wall Finishes (E)	04-28-2005	04-28-2005	2	50%	$6.61	$76,643	Complete patch & paint walls.
System:	Specialties (6)	Totals:	$3,896	$320,718
	167	Toilet Partitions (A)	04-28-2005	04-28-2005	2	10%	$1.68	$3,896	Replace all partitions to meet ADA Codes.
	Deficiency Detail by Building	FCI Version:  1.1.0
	Priorities 1-6	5/12/2009
	Priorities 1-6	Page 10 of 71

	University of Montana - Facilities Condition Inventory	Priorities	1
	Deficiency Detail by Building	2
	Site:	UM Missoula Main Campus	Area Correction:	1.16	Last Audit Date:	4/28/2005	3
	4
	Building:	Corbin Hall	Gross Area:	23,190	Sq Ft	Report Renewal Cost:	$680,157	5
	Category:	3A	Cost/Sq Ft:	$240.96	Deficiency Ratio:	12.2%	6
	Const. Date:	1927	Replacement Cost:	$5,587,862	7
	Comp.	System
	Entry #	Initial	Last	Unit	Renew	Replace
	Component	Entry	Update	Pri	%	Cost	Cost	Cost	Description
System:	HVAC System (7)	Totals:	$22,819	$522,703
	168	Heating (A)	04-28-2005	04-28-2005	2	10%	$9.84	$22,819	Replace heating control system and install building automation.
System:	Plumbing System (8)	Totals:	$98,267	$494,179
	169	Fixtures (A)	04-28-2005	04-28-2005	2	10%	$7.25	$16,813	Replace plumbing fixtures.
	170	Supply Piping (B)	04-28-2005	04-28-2005	2	25%	$8.22	$47,655	Replace supply piping.
	171	Waste Piping (C)	04-28-2005	04-28-2005	2	25%	$5.83	$33,799	Sanitary waste
System:	Electrical System (9)	Totals:	$62,295	$690,830
	172	Building Service (A)	04-28-2005	04-28-2005	2	1%	$7.78	$1,804	Meter replacement. 
	173	Lighting (B)	04-28-2005	04-28-2005	5	25%	$7.01	$40,640	Replace all lighting T-8 lights and Electronic ballarts. 
	174	Distribution (C)	04-28-2005	04-28-2005	2	10%	$8.56	$19,851	New panels, switches, outlets, some wire. 
System:	Safety System (11)	Totals:	$23,062	$308,659
	178	Exit/Emergency Lighting/Alarms (C)	04-28-2005	04-28-2005	3	20%	$4.50	$20,871	New Exit lights
	179	Asbestos/Hazardous Material (D)	04-28-2005	04-28-2005	4	35%	$0.27	$2,191	Asbestos removal in crawl spaces. 
	Deficiency Detail by Building	FCI Version:  1.1.0
	Priorities 1-6	5/12/2009
	Priorities 1-6	Page 11 of 71

	University of Montana - Facilities Condition Inventory	Priorities	1
	Deficiency Detail by Building	2
	Site:	UM Missoula Main Campus	Area Correction:	1.16	Last Audit Date:	4/28/2005	3
	4
	Building:	Davidson Honors College	Gross Area:	21,674	Sq Ft	Report Renewal Cost:	$41,993	5
	Category:	3C	Cost/Sq Ft:	$257.04	Deficiency Ratio:	0.8%	6
	Const. Date:	1996	Replacement Cost:	$5,571,518	7
	Comp.	System
	Entry #	Initial	Last	Unit	Renew	Replace
	Component	Entry	Update	Pri	%	Cost	Cost	Cost	Description
System:	HVAC System (7)	Totals:	$12,430	$710,474
	803	Cooling (C)	04-28-2005	04-28-2005	2	5%	$11.47	$12,430	A sandtrap needs to be installed on the ground water cooling system before
	 piping fails.
System:	Plumbing System (8)	Totals:	$19,810	$548,352
	804	Supply Piping (B)	04-28-2005	04-28-2005	2	10%	$9.14	$19,810	Hot water recirc. line has pinholes & corrosion. Needs to be replaced with 
	plastic flex tubing.
System:	Safety System (11)	Totals:	$9,753	$282,629
	805	Exit/Emergency Lighting/Alarms (C)	04-28-2005	04-28-2005	2	10%	$4.50	$9,753	Exit signs and emergency lighting needs backup batteries replaced 
	throughout building.
	Deficiency Detail by Building	FCI Version:  1.1.0
	Priorities 1-6	5/12/2009
	Priorities 1-6	Page 12 of 71

	University of Montana - Facilities Condition Inventory	Priorities	1
	Deficiency Detail by Building	2
	Site:	UM Missoula Main Campus	Area Correction:	1.16	Last Audit Date:	8/22/2007	3
	4
	Building:	Education Building	Gross Area:	27,770	Sq Ft	Report Renewal Cost:	$1,215,161	5
	Category:	3A	Cost/Sq Ft:	$240.96	Deficiency Ratio:	18.2%	6
	Const. Date:	1950	Replacement Cost:	$6,691,459	7
	Comp.	System
	Entry #	Initial	Last	Unit	Renew	Replace
	Component	Entry	Update	Pri	%	Cost	Cost	Cost	Description
System:	Foundations (1)	Totals:	$39,322	$148,292
	988	Exterior Steps/Retaining Walls (B)	08-22-2007	08-22-2007	2	80%	$1.77	$39,322	Cracked steps and separation is common.
System:	Envelope (2)	Totals:	$172,424	$486,530
	612	Exterior Walls (A)	04-28-2005	04-28-2005	2	15%	$4.66	$19,411	Terra Cotta repair on  all sides. Exterior also needs to be cleaned 
	tuckpointed and sealed.
	613	Exterior Windows (B)	04-28-2005	04-28-2005	2	100%	$5.51	$153,013	Windows are single pane wood frame and in need of repair
System:	Finishes (5)	Totals:	$115,121	$1,213,549
	617	Interior Walls (A)	04-28-2005	04-28-2005	2	10%	$12.18	$33,824	Cracks in plaster in various locations in hallways.
	619	Floor Finishes (D)	08-22-2007	04-28-2005	2	15%	$8.50	$35,407	Replace worn carpet in faculty and staff offices.
	620	Wall Finishes (E)	08-22-2007	04-28-2005	2	25%	$6.61	$45,890	Clean, grout and seal tile in hallways, bathrooms & Faculty offices
System:	Specialties (6)	Totals:	$19,522	$384,059
	989	Chalk/Tackboards/Cabinets (D)	08-22-2007	08-22-2007	2	10%	$7.03	$19,522	Still has blackboards.
System:	Plumbing System (8)	Totals:	$430,434	$591,779
	622	Fixtures (A)	08-22-2007	04-28-2005	2	20%	$7.25	$40,266	Fixtures are origional equipment and nearing the of useful life.
	623	Supply Piping (B)	04-28-2005	04-28-2005	2	100%	$8.22	$228,269	Piping is origional galvanized.
	624	Waste Piping (C)	04-28-2005	04-28-2005	2	100%	$5.83	$161,899	Waste system is cast with lead seals and is wroughted. Proper venting is 
	also needed.
	Deficiency Detail by Building	FCI Version:  1.1.0
	Priorities 1-6	5/12/2009
	Priorities 1-6	Page 13 of 71

	University of Montana - Facilities Condition Inventory	Priorities	1
	Deficiency Detail by Building	2
	Site:	UM Missoula Main Campus	Area Correction:	1.16	Last Audit Date:	8/22/2007	3
	4
	Building:	Education Building	Gross Area:	27,770	Sq Ft	Report Renewal Cost:	$1,215,161	5
	Category:	3A	Cost/Sq Ft:	$240.96	Deficiency Ratio:	18.2%	6
	Const. Date:	1950	Replacement Cost:	$6,691,459	7
	Comp.	System
	Entry #	Initial	Last	Unit	Renew	Replace
	Component	Entry	Update	Pri	%	Cost	Cost	Cost	Description
System:	Electrical System (9)	Totals:	$319,899	$827,268
	625	Building Service (A)	08-22-2007	04-28-2005	2	2%	$7.78	$4,321	Service needs a new meter.
	626	Lighting (B)	08-22-2007	04-28-2005	2	40%	$7.01	$77,867	Replace most of buildings lighting with electronic ballasts and T8 fixtures.
	627	Distribution (C)	08-22-2007	04-28-2005	2	100%	$8.56	$237,711	Replace old panels, switches and outlets.
System:	Safety System (11)	Totals:	$118,439	$369,619
	628	Egress (A)	04-28-2005	04-28-2005	3	25%	$2.66	$18,467	Fire enclose west staircase per UBC code.
	630	Exit/Emergency Lighting/Alarms (C)	04-28-2005	04-28-2005	3	80%	$4.50	$99,972	This building requires new exit signs, horns  & stroves.Doors aren't 
	connected to fire alarms.
	Deficiency Detail by Building	FCI Version:  1.1.0
	Priorities 1-6	5/12/2009
	Priorities 1-6	Page 14 of 71

	University of Montana - Facilities Condition Inventory	Priorities	1
	Deficiency Detail by Building	2
	Site:	UM Missoula Main Campus	Area Correction:	0.98	Last Audit Date:	8/2/2006	3
	4
	Building:	Fine Arts	Gross Area:	63,375	Sq Ft	Report Renewal Cost:	$2,573,278	5
	Category:	3A	Cost/Sq Ft:	$203.57	Deficiency Ratio:	19.9%	6
	Const. Date:	1935	Replacement Cost:	$12,901,249	7
	Comp.	System
	Entry #	Initial	Last	Unit	Renew	Replace
	Component	Entry	Update	Pri	%	Cost	Cost	Cost	Description
System:	Foundations (1)	Totals:	$57,069	$285,821
	909	Footings/Foundation Walls (A)	08-02-2006	08-02-2006	2	5%	$3.01	$9,538	surface of foundation in some areas needs to be repaired
	511	Exterior Steps/Retaining Walls (B)	08-02-2006	04-28-2005	2	50%	$1.50	$47,531	West side(Main Theatre) entrance & South Side: Replace worn out exterior
	 steps and seal concrete.
System:	Envelope (2)	Totals:	$231,952	$937,950
	512	Exterior Walls (A)	04-28-2005	04-28-2005	2	10%	$3.94	$24,970	Tuck point brick joints and repair terra-cotta tiles.
	513	Exterior Windows (B)	08-02-2006	04-28-2005	2	60%	$4.66	$177,196	Windows are original wood frame and are nearing end of life expectancy.
	514	Exterior Doors/Hatches (C)	08-02-2006	04-28-2005	2	25%	$0.80	$12,675	Change out to steel doors on South entrance. Kick plates needed on east side
	 entrance doors
	911	Interior Columns/Beams (D)	08-02-2006	08-02-2006	1	5%	$5.40	$17,111	on south of building entrance before stairway, horizontal beam needs more
	 head room.
System:	Floor System (3)	Totals:	$45,123	$1,164,833
	913	Floor Structure (A)	08-02-2006	08-02-2006	2	5%	$14.24	$45,123	under flooring on 4th floor. Needs to be replaced
System:	Roof System (4)	Totals:	$8,366	$344,760
	914	Covering (B)	08-02-2006	08-02-2006	2	5%	$2.64	$8,366	both east and west outside balconies need new roofing, especially close to 
	building
	Deficiency Detail by Building	FCI Version:  1.1.0
	Priorities 1-6	5/12/2009
	Priorities 1-6	Page 15 of 71

	University of Montana - Facilities Condition Inventory	Priorities	1
	Deficiency Detail by Building	2
	Site:	UM Missoula Main Campus	Area Correction:	0.98	Last Audit Date:	8/2/2006	3
	4
	Building:	Fine Arts	Gross Area:	63,375	Sq Ft	Report Renewal Cost:	$2,573,278	5
	Category:	3A	Cost/Sq Ft:	$203.57	Deficiency Ratio:	19.9%	6
	Const. Date:	1935	Replacement Cost:	$12,901,249	7
	Comp.	System
	Entry #	Initial	Last	Unit	Renew	Replace
	Component	Entry	Update	Pri	%	Cost	Cost	Cost	Description
System:	Finishes (5)	Totals:	$599,463	$2,339,805
	515	Interior Walls (A)	08-02-2006	04-28-2005	2	5%	$10.29	$32,606	Repair cracks in north hallway in theatre.
	516	Ceilings (B)	04-28-2005	04-28-2005	2	20%	$7.75	$98,231	Need paint. 
	517	Interior Doors/Hardware/Windows (C)	08-02-2006	04-28-2005	2	25%	$6.11	$96,805	Replace various damaged and worn out doors, hardware.
	518	Floor Finishes (D)	08-02-2006	04-28-2005	2	35%	$7.18	$159,261	Third and Fourth floors are cracked and tiles are worn beyond repair.
	519	Wall Finishes (E)	08-02-2006	04-28-2005	2	60%	$5.59	$212,560	Walls are dirty, discolered and still need paint and some patching.
System:	Specialties (6)	Totals:	$8,999	$740,220
	916	Toilet Partitions (A)	08-02-2006	08-02-2006	2	10%	$1.42	$8,999	Some partitions are old and worn out.
System:	HVAC System (7)	Totals:	$316,051	$1,206,660
	521	Heating (A)	08-02-2006	04-28-2005	2	50%	$8.31	$263,323	Damage wear-out of existing original unit heaters. Cast iron valves hard to 
	replace.
	522	Ventilating (B)	08-02-2006	04-28-2005	2	80%	$1.04	$52,728	New air handlers required  in the theatre.  Two exhaust, two return. No or 
	poor ventilation in FA
System:	Plumbing System (8)	Totals:	$548,701	$1,140,750
	523	Fixtures (A)	08-02-2006	04-28-2005	2	25%	$6.12	$96,964	Existing fixtures are very old-nearing end of expected life.
	524	Supply Piping (B)	08-02-2006	04-28-2005	2	60%	$6.95	$264,274	Replace existing galvanized with copper.
	525	Waste Piping (C)	08-02-2006	04-28-2005	2	60%	$4.93	$187,463	Replace existing metal with pvc.
System:	Electrical System (9)	Totals:	$500,093	$1,595,149
	526	Building Service (A)	04-28-2005	04-28-2005	2	20%	$6.58	$83,402	Update main distribution panel & service.
	527	Lighting (B)	04-28-2005	04-28-2005	2	50%	$5.92	$187,590	Replace old flourescents w. new T8 lamps & electronic ballasts.
	528	Distribution (C)	04-28-2005	04-28-2005	2	50%	$7.23	$229,101	Replace all old sub-panels w/ new panels.
	Deficiency Detail by Building	FCI Version:  1.1.0
	Priorities 1-6	5/12/2009
	Priorities 1-6	Page 16 of 71

	University of Montana - Facilities Condition Inventory	Priorities	1
	Deficiency Detail by Building	2
	Site:	UM Missoula Main Campus	Area Correction:	0.98	Last Audit Date:	8/2/2006	3
	4
	Building:	Fine Arts	Gross Area:	63,375	Sq Ft	Report Renewal Cost:	$2,573,278	5
	Category:	3A	Cost/Sq Ft:	$203.57	Deficiency Ratio:	19.9%	6
	Const. Date:	1935	Replacement Cost:	$12,901,249	7
	Comp.	System
	Entry #	Initial	Last	Unit	Renew	Replace
	Component	Entry	Update	Pri	%	Cost	Cost	Cost	Description
System:	Conveying (10)	Totals:	$206,761	$275,681
	529	Elevator/Lift (A)	08-02-2006	04-28-2005	2	75%	$4.35	$206,761	Existing unit is at the end of its reasonable expected life. Needs to be 
	replaced with new ADA acces
System:	Safety System (11)	Totals:	$50,700	$712,335
	532	Exit/Emergency Lighting/Alarms (C)	08-02-2006	04-28-2005	3	15%	$3.80	$36,124	Install new code compliant fire alarm panels & annunciators, connecting 
	fire doors w. closers etc,
	533	Asbestos/Hazardous Material (D)	04-28-2005	04-28-2005	2	100%	$0.23	$14,576	Existing building has asbestos in the ceilings, walls & floor tiles.
	Deficiency Detail by Building	FCI Version:  1.1.0
	Priorities 1-6	5/12/2009
	Priorities 1-6	Page 17 of 71

	University of Montana - Facilities Condition Inventory	Priorities	1
	Deficiency Detail by Building	2
	Site:	UM Missoula Main Campus	Area Correction:	1.16	Last Audit Date:	10/2/2007	3
	4
	Building:	Forestry	Gross Area:	23,310	Sq Ft	Report Renewal Cost:	$835,406	5
	Category:	4A	Cost/Sq Ft:	$261.44	Deficiency Ratio:	13.7%	6
	Const. Date:	1921	Replacement Cost:	$6,094,166	7
	Comp.	System
	Entry #	Initial	Last	Unit	Renew	Replace
	Component	Entry	Update	Pri	%	Cost	Cost	Cost	Description
System:	Foundations (1)	Totals:	$4,126	$377,389
	448	Exterior Steps/Retaining Walls (B)	04-28-2005	12-06-2006	2	10%	$1.77	$4,126	Main west stairs has cracked & settled
System:	Envelope (2)	Totals:	$56,363	$493,939
	449	Exterior Walls (A)	04-28-2005	04-28-2005	2	10%	$8.53	$19,883	Seal brick & repair terra-cotta.
	450	Exterior Windows (B)	04-28-2005	12-06-2006	2	50%	$3.13	$36,480	Glass has been replaced
System:	Roof System (4)	Totals:	$46,714	$248,485
	451	Covering (B)	04-28-2005	12-06-2006	2	10%	$5.99	$13,963	Re-paint roof soffit.
	452	Insulation (C)	04-28-2005	04-28-2005	5	50%	$2.81	$32,751	Additional insulation needed.
System:	Finishes (5)	Totals:	$111,386	$1,169,230
	1030	Interior Walls (A)	12-06-2006	12-06-2006	2	5%	$19.20	$22,378	Starting to show signs of wear.
	1031	Ceilings (B)	12-06-2006	12-06-2006	2	5%	$9.18	$10,699	Places starting to crack.
	453	Interior Doors/Hardware/Windows (C)	04-28-2005	12-06-2006	2	10%	$1.82	$4,242	Replace worn out door closers. 
	1032	Interior Doors/Hardware/Windows (C)	12-06-2006	12-06-2006	2	10%	$1.82	$4,242	some areas of heavy traffic showing signs of wear.
	1033	Floor Finishes (D)	12-06-2006	12-06-2006	2	15%	$10.06	$35,175	Carpet and Tarrazo showing signs of wear.
	1034	Wall Finishes (E)	12-06-2006	12-06-2006	2	15%	$9.91	$34,650	interior rooms need to be repainted.
System:	Specialties (6)	Totals:	$28,322	$396,736
	1036	Signage/Directories (B)	12-06-2006	12-06-2006	3	10%	$1.13	$2,634	new room signs
	1037	Fixed Seating/Risers (C)	04-28-2005	12-06-2006	2	10%	$3.99	$9,301	starting to show signs of wear.
	455	Chalk/Tackboards/Cabinets (D)	04-28-2005	12-06-2006	2	10%	$7.03	$16,387	Replace misc. sink cabinets.
	Deficiency Detail by Building	FCI Version:  1.1.0
	Priorities 1-6	5/12/2009
	Priorities 1-6	Page 18 of 71

	University of Montana - Facilities Condition Inventory	Priorities	1
	Deficiency Detail by Building	2
	Site:	UM Missoula Main Campus	Area Correction:	1.16	Last Audit Date:	10/2/2007	3
	4
	Building:	Forestry	Gross Area:	23,310	Sq Ft	Report Renewal Cost:	$835,406	5
	Category:	4A	Cost/Sq Ft:	$261.44	Deficiency Ratio:	13.7%	6
	Const. Date:	1921	Replacement Cost:	$6,094,166	7
	Comp.	System
	Entry #	Initial	Last	Unit	Renew	Replace
	Component	Entry	Update	Pri	%	Cost	Cost	Cost	Description
System:	HVAC System (7)	Totals:	$22,937	$431,468
	456	Heating (A)	04-28-2005	04-28-2005	2	10%	$9.84	$22,937	Repair traps & hand valves on radiators. 
System:	Plumbing System (8)	Totals:	$286,934	$657,342
	457	Fixtures (A)	04-28-2005	04-28-2005	2	5%	$10.41	$12,133	Origional porcelain fixtures are worn out. (Rms 301, 113, 107)
	458	Supply Piping (B)	04-28-2005	04-28-2005	2	80%	$9.63	$179,580	System is origonal galvanized and is nearing end of  life expectancy.
	459	Waste Piping (C)	04-28-2005	04-28-2005	2	50%	$8.17	$95,221	System is origonal cast and is nearing the end of life expectancy.
System:	Electrical System (9)	Totals:	$240,442	$450,815
	460	Lighting (B)	04-28-2005	04-28-2005	5	50%	$5.99	$69,813	Change out ballasts and and tubes with T8 system.
	991	Distribution (C)	10-02-2007	10-02-2007	2	100%	$7.32	$170,629	Panels are at end of useful life. Breakers are unsafe and replacements 
	unavailable.
System:	Safety System (11)	Totals:	$38,182	$258,042
	463	Exit/Emergency Lighting/Alarms (C)	04-28-2005	12-06-2006	3	90%	$1.82	$38,182	Replace all exit lights in building and bring up to code.(30%Install 
	emergency lighting and upgrade.new fire alarm panel.
	Deficiency Detail by Building	FCI Version:  1.1.0
	Priorities 1-6	5/12/2009
	Priorities 1-6	Page 19 of 71

	University of Montana - Facilities Condition Inventory	Priorities	1
	Deficiency Detail by Building	2
	Site:	UM Missoula Main Campus	Area Correction:	1.44	Last Audit Date:	12/6/2006	3
	4
	Building:	Forestry Greenhouse	Gross Area:	2,750	Sq Ft	Report Renewal Cost:	$144,862	5
	Category:	4A	Cost/Sq Ft:	$324.55	Deficiency Ratio:	16.2%	6
	Const. Date:	1951	Replacement Cost:	$892,512	7
	Comp.	System
	Entry #	Initial	Last	Unit	Renew	Replace
	Component	Entry	Update	Pri	%	Cost	Cost	Cost	Description
System:	Envelope (2)	Totals:	$21,230	$72,353
	440	Exterior Windows (B)	04-28-2005	12-06-2006	2	100%	$3.89	$10,698	Replace all greenhouse windows with new energy efficient glass.  
	441	Exterior Doors/Hatches (C)	04-28-2005	12-06-2006	2	100%	$3.83	$10,532	Doors are damaged/worn out from moisture.
System:	HVAC System (7)	Totals:	$46,420	$63,195
	442	Heating (A)	04-28-2005	12-06-2006	2	100%	$12.21	$33,578	Entire heat system is worn out.
	447	Ventilating (B)	04-28-2005	12-06-2006	2	100%	$4.67	$12,842	Fans are worn out and controls are obselete with no parts avail.
System:	Plumbing System (8)	Totals:	$60,747	$96,278
	443	Supply Piping (B)	04-28-2005	12-06-2006	2	100%	$11.95	$32,862	All supply piping is rotted galvanized and should be replaced.
	444	Waste Piping (C)	04-28-2005	12-06-2006	2	100%	$10.14	$27,885	All waste piping is rotted cast with lead seals and should be replaced.
System:	Electrical System (9)	Totals:	$16,465	$66,000
	445	Lighting (B)	04-28-2005	12-06-2006	2	50%	$7.43	$10,216	No Description
	446	Distribution (C)	04-28-2005	12-06-2006	2	25%	$9.09	$6,249	No Description
	Deficiency Detail by Building	FCI Version:  1.1.0
	Priorities 1-6	5/12/2009
	Priorities 1-6	Page 20 of 71

	University of Montana - Facilities Condition Inventory	Priorities	1
	Deficiency Detail by Building	2
	Site:	UM Missoula Main Campus	Area Correction:	0.98	Last Audit Date:	4/28/2005	3
	4
	Building:	Health Sciences	Gross Area:	62,964	Sq Ft	Report Renewal Cost:	$1,697,023	5
	Category:	4B	Cost/Sq Ft:	$243.20	Deficiency Ratio:	11.1%	6
	Const. Date:	1962	Replacement Cost:	$15,312,845	7
	Comp.	System
	Entry #	Initial	Last	Unit	Renew	Replace
	Component	Entry	Update	Pri	%	Cost	Cost	Cost	Description
System:	Envelope (2)	Totals:	$131,280	$1,111,944
	1	Exterior Windows (B)	04-28-2005	04-28-2005	5	25%	$3.12	$49,112	REPLACE SINGLE PANE WINDOWS
	2	Exterior Doors/Hatches (C)	04-28-2005	04-28-2005	2	50%	$2.61	$82,168	REPLACE ALL EXTERIOR DOORS
System:	Finishes (5)	Totals:	$311,766	$2,434,188
	11	Interior Walls (A)	04-28-2005	04-28-2005	2	5%	$14.75	$46,436	UPGRADE COLD ROOM
	3	Interior Doors/Hardware/Windows (C)	04-28-2005	04-28-2005	3	10%	$1.54	$9,696	REPLACE SOME HARDWARE
	54	Interior Doors/Hardware/Windows (C)	04-28-2005	04-28-2005	3	2%	$1.54	$1,939	REPLACE SOME HARDWARE
	4	Floor Finishes (D)	04-28-2005	04-28-2005	2	1%	$7.72	$4,861	REPAIR TILES NEEDING REPAIR
	5	Wall Finishes (E)	04-28-2005	04-28-2005	2	50%	$7.60	$239,263	INSTALL CORNER GUARDS 
	6	Wall Finishes (E)	04-28-2005	04-28-2005	2	2%	$7.60	$9,571	INSTALL CORNER GUARDS 
System:	Specialties (6)	Totals:	$347,171	$1,088,648
	7	Chalk/Tackboards/Cabinets (D)	04-28-2005	04-28-2005	2	2%	$5.94	$7,480	REPLACE LAB BENCHES AND CABINETS
	8	Chalk/Tackboards/Cabinets (D)	04-28-2005	04-28-2005	2	50%	$5.94	$187,003	REPLACE LAB BENCHES AND CABINETS
	9	Fume Hoods (E)	04-28-2005	04-28-2005	3	50%	$4.85	$152,688	REPLACE FUME HOODS
System:	HVAC System (7)	Totals:	$610,436	$1,932,365
	12	Heating (A)	04-28-2005	04-28-2005	2	70%	$13.85	$610,436	INSTALL BUILDING AUTOMATION SYSTEM
System:	Plumbing System (8)	Totals:	$87,645	$1,752,918
	16	Fixtures (A)	04-28-2005	04-28-2005	3	5%	$11.13	$35,039	REPLACE FIXTURES.
	17	Supply Piping (B)	04-28-2005	04-28-2005	2	5%	$9.05	$28,491	REPLACE VACUUM LINE
	18	Waste Piping (C)	04-28-2005	04-28-2005	2	5%	$7.66	$24,115	REPLACE WASTE LINES
	Deficiency Detail by Building	FCI Version:  1.1.0
	Priorities 1-6	5/12/2009
	Priorities 1-6	Page 21 of 71

	University of Montana - Facilities Condition Inventory	Priorities	1
	Deficiency Detail by Building	2
	Site:	UM Missoula Main Campus	Area Correction:	0.98	Last Audit Date:	4/28/2005	3
	4
	Building:	Health Sciences	Gross Area:	62,964	Sq Ft	Report Renewal Cost:	$1,697,023	5
	Category:	4B	Cost/Sq Ft:	$243.20	Deficiency Ratio:	11.1%	6
	Const. Date:	1962	Replacement Cost:	$15,312,845	7
	Comp.	System
	Entry #	Initial	Last	Unit	Renew	Replace
	Component	Entry	Update	Pri	%	Cost	Cost	Cost	Description
System:	Electrical System (9)	Totals:	$204,847	$1,135,871
	19	Building Service (A)	04-28-2005	04-28-2005	2	1%	$2.74	$1,725	REPLACE ELECTRIC METERS
	20	Lighting (B)	04-28-2005	04-28-2005	5	20%	$5.69	$71,653	REPLACE LIGHTS WITH ELECTRONIC BULLESTS T-8     LAMPS
	21	Distribution (C)	04-28-2005	04-28-2005	2	20%	$6.96	$87,646	REPLACE MOTOR CONTROL CENTER
	23	Distribution (C)	04-28-2005	04-28-2005	2	10%	$6.96	$43,823	REPLACE MOTOR CONTROL CENTER
System:	Safety System (11)	Totals:	$3,878	$588,713
	26	Exit/Emergency Lighting/Alarms (C)	04-28-2005	04-28-2005	3	2%	$1.54	$1,939	INSTALL EMERGENCY LIGHTING
	27	Exit/Emergency Lighting/Alarms (C)	04-28-2005	04-28-2005	3	2%	$1.54	$1,939	INSTALL EMERGENCY LIGHTING
	Deficiency Detail by Building	FCI Version:  1.1.0
	Priorities 1-6	5/12/2009
	Priorities 1-6	Page 22 of 71

	University of Montana - Facilities Condition Inventory	Priorities	1
	Deficiency Detail by Building	2
	Site:	UM Missoula Main Campus	Area Correction:	1.21	Last Audit Date:	3/28/2007	3
	4
	Building:	Heating Plant	Gross Area:	10,160	Sq Ft	Report Renewal Cost:	$202,342	5
	Category:	7A	Cost/Sq Ft:	$139.04	Deficiency Ratio:	14.3%	6
	Const. Date:	1923	Replacement Cost:	$1,412,748	7
	Comp.	System
	Entry #	Initial	Last	Unit	Renew	Replace
	Component	Entry	Update	Pri	%	Cost	Cost	Cost	Description
System:	Foundations (1)	Totals:	$16,764	$83,820
	489	Footings/Foundation Walls (A)	04-28-2005	03-28-2007	2	20%	$6.40	$13,005	WATERPROOF FOUNDATION.
	490	Exterior Steps/Retaining Walls (B)	04-28-2005	03-28-2007	2	20%	$1.85	$3,759	TUCKPOINT & SEAL CRACKS AT STEPS.
System:	Envelope (2)	Totals:	$85,039	$266,395
	491	Exterior Walls (A)	04-28-2005	03-28-2007	2	50%	$14.75	$74,930	TUCKPOINT, WATERPROOF, CLEAN AND PAINT.
	492	Exterior Windows (B)	04-28-2005	03-28-2007	2	50%	$0.34	$1,727	PAINT WINDOWS.
	493	Exterior Doors/Hatches (C)	04-28-2005	04-28-2005	2	50%	$1.65	$8,382	REPLACE DOORS.
System:	Finishes (5)	Totals:	$3,861	$64,414
	494	Wall Finishes (E)	04-28-2005	03-28-2007	2	100%	$0.38	$3,861	PAINT INTERIOR.
System:	Plumbing System (8)	Totals:	$31,166	$39,624
	552	Fixtures (A)	04-28-2005	03-28-2007	2	25%	$0.57	$1,448	Replace remainingl fixtures.
	553	Supply Piping (B)	04-28-2005	03-28-2007	2	50%	$0.81	$4,115	Replace worn out piping.
	554	Waste Piping (C)	04-28-2005	03-28-2007	2	100%	$2.52	$25,603	Replace most waste piping and rain water down spouts.
System:	Electrical System (9)	Totals:	$58,400	$72,644
	555	Building Service (A)	04-28-2005	04-28-2005	2	3%	$0.80	$244	Install power meter.
	556	Lighting (B)	04-28-2005	03-28-2007	5	90%	$2.86	$26,152	Replace lighting w/ new T8 lights.
	557	Distribution (C)	04-28-2005	03-28-2007	2	90%	$3.50	$32,004	New secondary panels, switch's and outlets.
System:	Safety System (11)	Totals:	$7,112	$117,551
	559	Exit/Emergency Lighting/Alarms (C)	04-28-2005	03-28-2007	2	100%	$0.70	$7,112	Install new emergency lighting, exit signs, alarms (replace battery system).
	Deficiency Detail by Building	FCI Version:  1.1.0
	Priorities 1-6	5/12/2009
	Priorities 1-6	Page 23 of 71

	University of Montana - Facilities Condition Inventory	Priorities	1
	Deficiency Detail by Building	2
	Site:	UM Missoula Main Campus	Area Correction:	1.44	Last Audit Date:	2/14/2007	3
	4
	Building:	International Programs	Gross Area:	6,853	Sq Ft	Report Renewal Cost:	$206,072	5
	Category:	3A	Cost/Sq Ft:	$299.12	Deficiency Ratio:	10.1%	6
	Const. Date:	1937	Replacement Cost:	$2,049,869	7
	Comp.	System
	Entry #	Initial	Last	Unit	Renew	Replace
	Component	Entry	Update	Pri	%	Cost	Cost	Cost	Description
System:	Foundations (1)	Totals:	$14,336	$45,367
	944	Footings/Foundation Walls (A)	02-14-2007	02-14-2007	2	10%	$4.42	$3,029	settling/cracks in each of four corners
	499	Exterior Steps/Retaining Walls (B)	04-28-2005	04-28-2005	2	75%	$2.20	$11,307	Steps and brick fascia need repair and replacement in places on main 
	entrance. Also needs to be seal
System:	Envelope (2)	Totals:	$56,504	$148,984
	495	Exterior Walls (A)	04-28-2005	02-14-2007	2	10%	$5.79	$3,968	Tuckpoint, clean & seal brick.
	496	Exterior Windows (B)	04-28-2005	04-28-2005	2	100%	$6.84	$46,875	All windows are origional wood frame.
	497	Exterior Doors/Hatches (C)	04-28-2005	04-28-2005	2	70%	$1.18	$5,661	Front entry doors and east entry door needs replacement. Wood frame in 
	poor condition.
System:	Finishes (5)	Totals:	$25,467	$371,707
	946	Ceilings (B)	02-14-2007	02-14-2007	2	5%	$11.39	$3,903	several stained tiles
	947	Interior Doors/Hardware/Windows (C)	02-14-2007	02-14-2007	2	5%	$8.97	$3,074	Interior doors are cracking and need to be filled.
	948	Floor Finishes (D)	02-14-2007	02-14-2007	2	10%	$10.56	$7,237	Several sections of flooring are showing wear.
	949	Wall Finishes (E)	02-14-2007	02-14-2007	2	20%	$8.21	$11,253	classrooms and some offices need touch painting or new paint.
System:	HVAC System (7)	Totals:	$19,176	$191,747
	950	Heating (A)	02-14-2007	02-14-2007	4	10%	$12.21	$8,368	Heating and cooling need better regulation
	951	Ventilating (B)	02-14-2007	02-14-2007	4	10%	$1.53	$1,049	Heating and cooling need better regulation.
	952	Cooling (C)	02-14-2007	02-14-2007	4	10%	$14.24	$9,759	Heating and cooling need better regulation.
System:	Plumbing System (8)	Totals:	$72,450	$181,262
	503	Supply Piping (B)	04-28-2005	04-28-2005	2	100%	$10.21	$69,969	Original galvanized piping.
	953	Waste Piping (C)	02-14-2007	02-14-2007	2	5%	$7.24	$2,481	waster piping is original and near the end of its life expectancy.
	Deficiency Detail by Building	FCI Version:  1.1.0
	Priorities 1-6	5/12/2009
	Priorities 1-6	Page 24 of 71

	University of Montana - Facilities Condition Inventory	Priorities	1
	Deficiency Detail by Building	2
	Site:	UM Missoula Main Campus	Area Correction:	1.44	Last Audit Date:	2/14/2007	3
	4
	Building:	International Programs	Gross Area:	6,853	Sq Ft	Report Renewal Cost:	$206,072	5
	Category:	3A	Cost/Sq Ft:	$299.12	Deficiency Ratio:	10.1%	6
	Const. Date:	1937	Replacement Cost:	$2,049,869	7
	Comp.	System
	Entry #	Initial	Last	Unit	Renew	Replace
	Component	Entry	Update	Pri	%	Cost	Cost	Cost	Description
System:	Electrical System (9)	Totals:	$16,224	$253,424
	510	Building Service (A)	04-28-2005	02-14-2007	1	10%	$9.66	$6,620	Transformer need lugs tightened.
	506	Lighting (B)	04-28-2005	04-28-2005	2	10%	$8.70	$5,962	Light change-out where necesary.
	507	Distribution (C)	04-28-2005	02-14-2007	1	5%	$10.63	$3,642	replace upstairs panel - kitchen needs GFI.
System:	Safety System (11)	Totals:	$1,915	$113,212
	509	Exit/Emergency Lighting/Alarms (C)	04-28-2005	04-28-2005	3	5%	$5.59	$1,915	No exit signs or emergency lighting presently exists within the building.
	Deficiency Detail by Building	FCI Version:  1.1.0
	Priorities 1-6	5/12/2009
	Priorities 1-6	Page 25 of 71

	University of Montana - Facilities Condition Inventory	Priorities	1
	Deficiency Detail by Building	2
	Site:	UM Missoula Main Campus	Area Correction:	1.21	Last Audit Date:	9/21/2006	3
	4
	Building:	Jeanette Rankin Hall	Gross Area:	16,532	Sq Ft	Report Renewal Cost:	$1,309,361	5
	Category:	3A	Cost/Sq Ft:	$251.34	Deficiency Ratio:	31.5%	6
	Const. Date:	1909	Replacement Cost:	$4,155,153	7
	Comp.	System
	Entry #	Initial	Last	Unit	Renew	Replace
	Component	Entry	Update	Pri	%	Cost	Cost	Cost	Description
System:	Foundations (1)	Totals:	$19,913	$92,083
	363	Footings/Foundation Walls (A)	04-28-2005	09-21-2006	2	20%	$3.71	$12,267	NO. & SO. Foundation Walls need to be waterproofed. More settlement 
	cracks forming.
	364	Exterior Steps/Retaining Walls (B)	04-28-2005	09-21-2006	2	25%	$1.85	$7,646	Steps need sealing. Mortar joints redone. I-Beam underneath steps is 
	rusting.
System:	Envelope (2)	Totals:	$99,076	$302,040
	365	Exterior Walls (A)	04-28-2005	09-21-2006	2	5%	$4.86	$4,017	TUCK POINT & SEAL BRICKS. SETTLING CRACKS NOTED IN 
	BRICKS ON S/E & S/W WALL.
	366	Exterior Windows (B)	04-28-2005	09-21-2006	2	100%	$5.75	$95,059	REPLACE ALL EXTERIOR WINDOWS.
System:	Floor System (3)	Totals:	$149,540	$375,111
	368	Floor Structure (A)	04-28-2005	09-21-2006	2	50%	$17.58	$145,316	Basement Floor squeaks and sinks, needs re-building.Replace 
	mezanine(20%)
	369	Stair Treads/Risers (B)	04-28-2005	09-21-2006	2	5%	$5.11	$4,224	PARTIALLY WORN STAIR TREAD.
System:	Roof System (4)	Totals:	$78,858	$111,095
	370	Covering (B)	04-28-2005	09-21-2006	2	100%	$3.25	$53,729	Roof replacement on list.
	371	Insulation (C)	04-28-2005	09-21-2006	2	100%	$1.52	$25,129	Replace all attic insulation - may contain vermiculite
	Deficiency Detail by Building	FCI Version:  1.1.0
	Priorities 1-6	5/12/2009
	Priorities 1-6	Page 26 of 71

	University of Montana - Facilities Condition Inventory	Priorities	1
	Deficiency Detail by Building	2
	Site:	UM Missoula Main Campus	Area Correction:	1.21	Last Audit Date:	9/21/2006	3
	4
	Building:	Jeanette Rankin Hall	Gross Area:	16,532	Sq Ft	Report Renewal Cost:	$1,309,361	5
	Category:	3A	Cost/Sq Ft:	$251.34	Deficiency Ratio:	31.5%	6
	Const. Date:	1909	Replacement Cost:	$4,155,153	7
	Comp.	System
	Entry #	Initial	Last	Unit	Renew	Replace
	Component	Entry	Update	Pri	%	Cost	Cost	Cost	Description
System:	Finishes (5)	Totals:	$192,458	$753,529
	372	Interior Walls (A)	04-28-2005	09-21-2006	2	25%	$12.70	$52,489	More plaster cracks showing up.
	373	Ceilings (B)	04-28-2005	09-21-2006	2	25%	$9.57	$39,553	Install suspended ceilings - coordinate with Historical Preservation 
	Committee.
	374	Interior Doors/Hardware/Windows (C)	04-28-2005	09-21-2006	2	25%	$7.54	$31,163	Install fire rated doors and check with Historical Committee about transom.
	376	Floor Finishes (D)	04-28-2005	09-21-2006	2	20%	$8.87	$29,328	REPLACE WORN OUT CARPET.
	377	Wall Finishes (E)	04-28-2005	09-21-2006	2	35%	$6.90	$39,925	CLASS ROOMS HAVE BEEN DONE. THE REST OF THE BUILDING 
	INTERIOR IS CRACKING AND PEELING. 
System:	Specialties (6)	Totals:	$9,547	$238,391
	378	Toilet Partitions (A)	04-28-2005	09-21-2006	2	33%	$1.75	$9,547	PARTITIONS ARE WOOD AND NEED REPLACEMENT.
System:	HVAC System (7)	Totals:	$5,290	$388,667
	920	Ventilating (B)	09-21-2006	09-21-2006	1	25%	$1.28	$5,290	Ventilation needed in mechanical room under entrance steps.
System:	Plumbing System (8)	Totals:	$286,269	$367,506
	382	Fixtures (A)	04-28-2005	09-21-2006	1	35%	$7.56	$43,744	Faucets in men's bathroom not ADA.
	383	Supply Piping (B)	04-28-2005	09-21-2006	2	100%	$8.58	$141,845	PIPING IS WORN OUT GALV OR BLACK IRON. NEEDS 
	REPLACEMENT.
	384	Waste Piping (C)	04-28-2005	09-21-2006	2	100%	$6.09	$100,680	ORIGIONAL WASTE SYSTEM IS CAST IRON.
	Deficiency Detail by Building	FCI Version:  1.1.0
	Priorities 1-6	5/12/2009
	Priorities 1-6	Page 27 of 71

	University of Montana - Facilities Condition Inventory	Priorities	1
	Deficiency Detail by Building	2
	Site:	UM Missoula Main Campus	Area Correction:	1.21	Last Audit Date:	9/21/2006	3
	4
	Building:	Jeanette Rankin Hall	Gross Area:	16,532	Sq Ft	Report Renewal Cost:	$1,309,361	5
	Category:	3A	Cost/Sq Ft:	$251.34	Deficiency Ratio:	31.5%	6
	Const. Date:	1909	Replacement Cost:	$4,155,153	7
	Comp.	System
	Entry #	Initial	Last	Unit	Renew	Replace
	Component	Entry	Update	Pri	%	Cost	Cost	Cost	Description
System:	Electrical System (9)	Totals:	$372,508	$513,649
	385	Building Service (A)	04-28-2005	09-21-2006	2	100%	$8.12	$134,240	INSTALL NEW SERVICE. 
	386	Lighting (B)	04-28-2005	09-21-2006	5	75%	$7.31	$90,637	INSTALL ELECTRONIC BALLASTS AND T8 LAMPS..T-12s are 
	becoming obsolete.
	387	Distribution (C)	04-28-2005	09-21-2006	2	100%	$8.93	$147,631	INSTALL NEW SECONDARY ELECTRICAL SYSTEM, SWITCHES 
	AND OUTLETS.
System:	Safety System (11)	Totals:	$95,902	$229,464
	389	Egress (A)	04-28-2005	09-21-2006	2	30%	$2.77	$13,738	(25%)BASEMENT TO FIRST FLOOR STAIRS NEED 
	REPLACEMENT.(5%)AREAS OF RESCUE ASSISTANCE NEEDED.
	391	Exit/Emergency Lighting/Alarms (C)	04-28-2005	09-21-2006	3	100%	$4.69	$77,535	exit lights, emergency lighting, smoke detectors and fire alarm system
	392	Asbestos/Hazardous Material (D)	04-28-2005	09-21-2006	3	100%	$0.28	$4,629	REMOVE ASBESTOS THROUGHOUT BUILDING.
	Deficiency Detail by Building	FCI Version:  1.1.0
	Priorities 1-6	5/12/2009
	Priorities 1-6	Page 28 of 71

	University of Montana - Facilities Condition Inventory	Priorities	1
	Deficiency Detail by Building	2
	Site:	UM Missoula Main Campus	Area Correction:	0.98	Last Audit Date:	6/7/2006	3
	4
	Building:	Law	Gross Area:	58,750	Sq Ft	Report Renewal Cost:	$2,889,092	5
	Category:	3B	Cost/Sq Ft:	$214.87	Deficiency Ratio:	22.9%	6
	Const. Date:	1962	Replacement Cost:	$12,624,200	7
	Comp.	System
	Entry #	Initial	Last	Unit	Renew	Replace
	Component	Entry	Update	Pri	%	Cost	Cost	Cost	Description
System:	Foundations (1)	Totals:	$13,190	$220,313
	874	Footings/Foundation Walls (A)	06-07-2006	06-07-2006	2	5%	$3.01	$8,842	Sections of Concrete Masonry Unit (CMU) are showing signs of wear.
	875	Exterior Steps/Retaining Walls (B)	06-07-2006	06-07-2006	2	10%	$0.74	$4,348	Section of concrete ramp on north end is totally separating.  Damage might
	 cause safety issue.
System:	Envelope (2)	Totals:	$301,365	$876,550
	719	Exterior Walls (A)	04-28-2005	04-28-2005	2	2%	$3.94	$4,630	Seal concrete eve around building from further cracking. Repair cracks in 
	concrete on SW wall just v
	876	Exterior Walls (A)	06-07-2006	06-07-2006	2	2%	$3.94	$4,630	Sections of brick work on south west face is breaking off, possible from roof
	 drain.
	720	Exterior Windows (B)	06-07-2006	04-28-2005	5	40%	$5.48	$128,780	Re-glaze single pane windows low E.
	877	Exterior Windows (B)	06-07-2006	06-07-2006	2	50%	$5.48	$160,975	window glazing starting to wear out. No replace parts available.
	901	Exterior Doors/Hatches (C)	06-07-2006	06-07-2006	2	5%	$0.80	$2,350	A couple of metal doors need to be treated and painted.
System:	Roof System (4)	Totals:	$186,619	$299,625
	722	Covering (B)	04-28-2005	04-28-2005	2	5%	$2.29	$6,727	Replace flashing at west EPDM section fo roof.
	879	Covering (B)	06-07-2006	06-07-2006	2	80%	$2.29	$107,630	Upper section 100%, ballast section 50%
	881	Insulation (C)	06-07-2006	06-07-2006	5	100%	$1.23	$72,262	Very little or no insulation was identified in roof system.
	Deficiency Detail by Building	FCI Version:  1.1.0
	Priorities 1-6	5/12/2009
	Priorities 1-6	Page 29 of 71

	University of Montana - Facilities Condition Inventory	Priorities	1
	Deficiency Detail by Building	2
	Site:	UM Missoula Main Campus	Area Correction:	0.98	Last Audit Date:	6/7/2006	3
	4
	Building:	Law	Gross Area:	58,750	Sq Ft	Report Renewal Cost:	$2,889,092	5
	Category:	3B	Cost/Sq Ft:	$214.87	Deficiency Ratio:	22.9%	6
	Const. Date:	1962	Replacement Cost:	$12,624,200	7
	Comp.	System
	Entry #	Initial	Last	Unit	Renew	Replace
	Component	Entry	Update	Pri	%	Cost	Cost	Cost	Description
System:	Finishes (5)	Totals:	$164,206	$2,003,963
	903	Interior Walls (A)	06-07-2006	06-07-2006	2	5%	$9.36	$27,495	Some places where sheetrock is damaged and needs to be replaced.
	882	Ceilings (B)	06-07-2006	06-07-2006	2	5%	$7.05	$20,709	A few locations where water has damaged/stained ceiling tile.
	884	Interior Doors/Hardware/Windows (C)	06-07-2006	06-07-2006	2	5%	$6.11	$17,948	some doors need refurbishing, new hardware and new keys
	885	Floor Finishes (D)	06-07-2006	06-07-2006	2	10%	$6.53	$38,364	Large area on first floor where 'something' is happening to cause a 
	swelling up of the tile.
	887	Wall Finishes (E)	06-07-2006	06-07-2006	2	20%	$5.08	$59,690	The wood wall panels and trim in several lecture room need to be 
	reconditioned
System:	HVAC System (7)	Totals:	$1,463,628	$1,626,788
	889	Heating (A)	06-07-2006	06-07-2006	2	100%	$13.85	$813,688	Heating system has reached useful life and needs to be replaced.
	727	Ventilating (B)	06-07-2006	04-28-2005	2	33%	$4.16	$80,652	Replace existing pvc pipes on heat pump system w. copper. Replace 7 old 
	heat pumps.
	891	Cooling (C)	06-07-2006	06-07-2006	2	100%	$9.69	$569,288	Cooling system is worn out and needs to be replaced.
System:	Plumbing System (8)	Totals:	$145,935	$1,231,400
	893	Fixtures (A)	06-07-2006	06-07-2006	2	15%	$7.76	$68,385	Bathroom fixtures need to be replaced.
	894	Supply Piping (B)	06-07-2006	06-07-2006	2	10%	$7.72	$45,355	Original supply lines are over 40 years old and sections need to be 
	replaced.
	895	Waste Piping (C)	06-07-2006	06-07-2006	2	10%	$5.48	$32,195	Original systems is over 40 years old and sections need to be replaced.
System:	Electrical System (9)	Totals:	$433,199	$1,615,038
	731	Building Service (A)	04-28-2005	04-28-2005	2	2%	$6.58	$7,732	Replace electric meters.
	732	Lighting (B)	06-07-2006	04-28-2005	5	60%	$6.65	$234,412	Upgrade to energy efficient T8 light fixtures.
	897	Distribution (C)	06-07-2006	06-07-2006	2	40%	$8.13	$191,055	Portions of system is worn out and needs to be replaced.
	Deficiency Detail by Building	FCI Version:  1.1.0
	Priorities 1-6	5/12/2009
	Priorities 1-6	Page 30 of 71

	University of Montana - Facilities Condition Inventory	Priorities	1
	Deficiency Detail by Building	2
	Site:	UM Missoula Main Campus	Area Correction:	0.98	Last Audit Date:	6/7/2006	3
	4
	Building:	Law	Gross Area:	58,750	Sq Ft	Report Renewal Cost:	$2,889,092	5
	Category:	3B	Cost/Sq Ft:	$214.87	Deficiency Ratio:	22.9%	6
	Const. Date:	1962	Replacement Cost:	$12,624,200	7
	Comp.	System
	Entry #	Initial	Last	Unit	Renew	Replace
	Component	Entry	Update	Pri	%	Cost	Cost	Cost	Description
System:	Safety System (11)	Totals:	$180,950	$660,350
	898	Exit/Emergency Lighting/Alarms (C)	06-07-2006	06-07-2006	1	75%	$3.80	$167,438	all exit signs need to be replaced.
	737	Asbestos/Hazardous Material (D)	04-28-2005	04-28-2005	4	100%	$0.23	$13,512	Replace existing asbestos floor tiles.
	Deficiency Detail by Building	FCI Version:  1.1.0
	Priorities 1-6	5/12/2009
	Priorities 1-6	Page 31 of 71

	University of Montana - Facilities Condition Inventory	Priorities	1
	Deficiency Detail by Building	2
	Site:	UM Missoula Main Campus	Area Correction:	0.94	Last Audit Date:	6/20/2007	3
	4
	Building:	Liberal Arts	Gross Area:	100,713	Sq Ft	Report Renewal Cost:	$2,595,818	5
	Category:	3A	Cost/Sq Ft:	$195.26	Deficiency Ratio:	13.2%	6
	Const. Date:	1954	Replacement Cost:	$19,665,220	7
	Comp.	System
	Entry #	Initial	Last	Unit	Renew	Replace
	Component	Entry	Update	Pri	%	Cost	Cost	Cost	Description
System:	Foundations (1)	Totals:	$43,508	$435,080
	28	Exterior Steps/Retaining Walls (B)	04-28-2005	04-28-2005	2	30%	$1.44	$43,508	STEPS NEED REPAIR
System:	Envelope (2)	Totals:	$506,496	$1,429,117
	29	Exterior Walls (A)	04-28-2005	04-28-2005	2	2%	$3.78	$7,614	TUCKPOINT AND WATERPROOF
	30	Exterior Walls (A)	04-28-2005	04-28-2005	2	10%	$3.78	$38,070	TUCKPOINT AND WATERPROOF
	978	Exterior Windows (B)	06-20-2007	06-20-2007	2	100%	$4.46	$449,180	Residential windows, not for commercial use. Worn out.
	31	Exterior Doors/Hatches (C)	04-28-2005	04-28-2005	2	15%	$0.77	$11,632	REPLACE ALL ENTRY DOORS
System:	Floor System (3)	Totals:	$68,787	$1,774,563
	979	Floor Structure (A)	06-20-2007	06-20-2007	2	5%	$13.66	$68,787	Starting to show signs of cracking.
System:	Roof System (4)	Totals:	$373,645	$525,722
	33	Covering (B)	04-28-2005	04-28-2005	2	100%	$2.53	$254,804	REPLACE ROOFING WITH HYPOLON
	980	Insulation (C)	06-20-2007	06-20-2007	3	100%	$1.18	$118,841	None installed.
System:	Finishes (5)	Totals:	$811,757	$3,566,247
	981	Interior Walls (A)	06-20-2007	06-20-2007	2	10%	$9.87	$99,404	Minor scratches throughout.
	982	Ceilings (B)	06-20-2007	06-20-2007	2	30%	$7.44	$224,791	lots of sections have water stains or are damaged.
	34	Interior Doors/Hardware/Windows (C)	04-28-2005	04-28-2005	3	30%	$5.86	$177,053	REPLACE PANIC DEVICES, CLOSURES
	35	Interior Doors/Hardware/Windows (C)	04-28-2005	04-28-2005	2	1%	$5.86	$5,902	REPLACE PANIC DEVICES, CLOSURES
	36	Floor Finishes (D)	04-28-2005	04-28-2005	2	5%	$6.89	$34,696	CARPET REPLACEMENT
	983	Wall Finishes (E)	06-20-2007	06-20-2007	2	50%	$5.36	$269,911	All bathrooms need painting. Corridors okay.
	Deficiency Detail by Building	FCI Version:  1.1.0
	Priorities 1-6	5/12/2009
	Priorities 1-6	Page 32 of 71

	University of Montana - Facilities Condition Inventory	Priorities	1
	Deficiency Detail by Building	2
	Site:	UM Missoula Main Campus	Area Correction:	0.94	Last Audit Date:	6/20/2007	3
	4
	Building:	Liberal Arts	Gross Area:	100,713	Sq Ft	Report Renewal Cost:	$2,595,818	5
	Category:	3A	Cost/Sq Ft:	$195.26	Deficiency Ratio:	13.2%	6
	Const. Date:	1954	Replacement Cost:	$19,665,220	7
	Comp.	System
	Entry #	Initial	Last	Unit	Renew	Replace
	Component	Entry	Update	Pri	%	Cost	Cost	Cost	Description
System:	Specialties (6)	Totals:	$115,669	$1,127,986
	37	Toilet Partitions (A)	04-28-2005	04-28-2005	2	10%	$1.36	$13,697	REPLACE ALL TOILET PARTITIONS
	984	Signage/Directories (B)	06-20-2007	06-20-2007	3	10%	$0.91	$9,165	No Braille, evacuation maps.
	38	Fixed Seating/Risers (C)	04-28-2005	04-28-2005	2	25%	$3.23	$81,326	REPLACE FIXED SEATING ROOM 11
	39	Chalk/Tackboards/Cabinets (D)	04-28-2005	04-28-2005	2	2%	$5.70	$11,481	REPLACE CHALK BOARDS
System:	HVAC System (7)	Totals:	$33,205	$1,839,019
	40	Heating (A)	04-28-2005	04-28-2005	2	1%	$7.97	$8,027	MAINTENANCE ON VALVING
	985	Ventilating (B)	06-20-2007	06-20-2007	2	25%	$1.00	$25,178	More air needs to be routed through building.
System:	Plumbing System (8)	Totals:	$83,038	$1,739,314
	43	Fixtures (A)	04-28-2005	04-28-2005	3	10%	$5.88	$59,219	REPLACE ALL FIXTURES
	44	Waste Piping (C)	04-28-2005	04-28-2005	2	5%	$4.73	$23,819	REPLACE WASTE PIPING ON DRINKING FOUNTAINS AND 
	TOILETS AS NEEDED
System:	Electrical System (9)	Totals:	$425,815	$2,431,212
	45	Lighting (B)	06-20-2007	04-28-2005	5	50%	$5.68	$286,025	INSTALL ELECTRONIC BALLASTS AND T8 LAMPS
	46	Distribution (C)	06-20-2007	04-28-2005	2	10%	$6.94	$69,895	East side service needs NEW CT METERS
	47	Distribution (C)	04-28-2005	04-28-2005	2	10%	$6.94	$69,895	Westside Services needs NEW CT METERS
System:	Conveying (10)	Totals:	$41,997	$419,973
	986	Elevator/Lift (A)	06-20-2007	06-20-2007	2	10%	$4.17	$41,997	six years old
System:	Safety System (11)	Totals:	$91,901	$1,085,686
	50	Exit/Emergency Lighting/Alarms (C)	06-20-2007	04-28-2005	2	25%	$3.65	$91,901	Quite a few areas still don't have lighting.
	Deficiency Detail by Building	FCI Version:  1.1.0
	Priorities 1-6	5/12/2009
	Priorities 1-6	Page 33 of 71

	University of Montana - Facilities Condition Inventory	Priorities	1
	Deficiency Detail by Building	2
	Site:	UM Missoula Main Campus	Area Correction:	0.93	Last Audit Date:	7/16/2008	3
	4
	Building:	Mansfield Library	Gross Area:	220,075	Sq Ft	Report Renewal Cost:	$5,282,043	5
	Category:	3B	Cost/Sq Ft:	$203.91	Deficiency Ratio:	11.8%	6
	Const. Date:	1973	Replacement Cost:	$44,877,694	7
	Comp.	System
	Entry #	Initial	Last	Unit	Renew	Replace
	Component	Entry	Update	Pri	%	Cost	Cost	Cost	Description
System:	Foundations (1)	Totals:	$15,625	$783,467
	993	Exterior Steps/Retaining Walls (B)	07-16-2008	07-16-2008	2	10%	$0.71	$15,625	South load dock needs touch up. Pads are worn out
System:	Envelope (2)	Totals:	$155,593	$3,114,061
	55	Exterior Walls (A)	07-16-2008	04-28-2005	2	5%	$3.74	$41,154	Clean and seal exterior aggregate and caulk PC panels.
	56	Exterior Windows (B)	07-16-2008	04-28-2005	5	10%	$5.20	$114,439	CHANGE OUT SINGLE PANE WINDOWS AND REPLACE WITH low 
	E PAINE .Subframe needs paint
System:	Floor System (3)	Totals:	$474,482	$3,838,108
	57	Stair Treads/Risers (B)	07-16-2008	04-28-2005	2	5%	$3.92	$43,135	Patch treads.
	58	Stair Treads/Risers (B)	04-28-2005	04-28-2005	3	50%	$3.92	$431,347	R/R STAIR BALLISTER
System:	Roof System (4)	Totals:	$737,252	$1,065,163
	995	Covering (B)	07-16-2008	07-16-2008	2	100%	$2.18	$479,764	Several locations where gravel covering has grinded into the roof surface.
	996	Insulation (C)	07-16-2008	07-16-2008	5	100%	$1.17	$257,488	not sure of whether there is ANY insulation for roofing area
System:	Finishes (5)	Totals:	$1,927,879	$7,123,828
	59	Interior Walls (A)	07-16-2008	04-28-2005	2	2%	$8.88	$39,085	CRACKS & MASONARY WALLS AND RAILS ACROSS STONE 
	PICTURES
	60	Ceilings (B)	07-16-2008	04-28-2005	2	100%	$6.69	$1,472,302	obsolete
	61	Floor Finishes (D)	07-16-2008	04-28-2005	2	15%	$6.19	$204,340	Replace worn carpeting between stacks
	998	Wall Finishes (E)	07-16-2008	07-16-2008	2	20%	$4.82	$212,152	Many interior walls need to be painted.
	Deficiency Detail by Building	FCI Version:  1.1.0
	Priorities 1-6	5/12/2009
	Priorities 1-6	Page 34 of 71

	University of Montana - Facilities Condition Inventory	Priorities	1
	Deficiency Detail by Building	2
	Site:	UM Missoula Main Campus	Area Correction:	0.93	Last Audit Date:	7/16/2008	3
	4
	Building:	Mansfield Library	Gross Area:	220,075	Sq Ft	Report Renewal Cost:	$5,282,043	5
	Category:	3B	Cost/Sq Ft:	$203.91	Deficiency Ratio:	11.8%	6
	Const. Date:	1973	Replacement Cost:	$44,877,694	7
	Comp.	System
	Entry #	Initial	Last	Unit	Renew	Replace
	Component	Entry	Update	Pri	%	Cost	Cost	Cost	Description
System:	HVAC System (7)	Totals:	$908,030	$5,783,571
	301	Ventilating (B)	07-16-2008	04-28-2005	2	30%	$3.94	$260,129	Replace failed humidification system. Additional ductwork for remodel 
	work
	62	Cooling (C)	07-16-2008	04-28-2005	2	32%	$9.20	$647,901	Replace old worn out chiller with two new chillers.  DDC is 15 yrs old and 
	no longer supported.  Need AC for remodelled rooms.
System:	Conveying (10)	Totals:	$16,506	$825,281
	1000	Elevator/Lift (A)	07-16-2008	07-16-2008	2	2%	$3.75	$16,506	wall panels need repair work
System:	Safety System (11)	Totals:	$1,046,676	$2,348,200
	1001	Extinguishing System (B)	07-16-2008	07-16-2008	1	100%	$2.59	$569,994	replace all smoke dedectors
	1002	Exit/Emergency Lighting/Alarms (C)	07-16-2008	07-16-2008	1	60%	$3.61	$476,682	No directions, no phones
	Deficiency Detail by Building	FCI Version:  1.1.0
	Priorities 1-6	5/12/2009
	Priorities 1-6	Page 35 of 71

	University of Montana - Facilities Condition Inventory	Priorities	1
	Deficiency Detail by Building	2
	Site:	UM Missoula Main Campus	Area Correction:	1.21	Last Audit Date:	4/18/2007	3
	4
	Building:	Mathematics	Gross Area:	18,610	Sq Ft	Report Renewal Cost:	$1,144,408	5
	Category:	3A	Cost/Sq Ft:	$209.31	Deficiency Ratio:	29.4%	6
	Const. Date:	1903	Replacement Cost:	$3,895,259	7
	Comp.	System
	Entry #	Initial	Last	Unit	Renew	Replace
	Component	Entry	Update	Pri	%	Cost	Cost	Cost	Description
System:	Foundations (1)	Totals:	$46,590	$103,658
	338	Footings/Foundation Walls (A)	04-28-2005	04-18-2007	2	60%	$3.71	$41,426	Repair & waterproof South, East andNorth foundations.
	960	Exterior Steps/Retaining Walls (B)	04-18-2007	04-18-2007	2	15%	$1.85	$5,164	Tuck pointing is needed in several spots.
System:	Envelope (2)	Totals:	$161,275	$340,005
	339	Exterior Walls (A)	04-28-2005	04-18-2007	2	60%	$4.86	$54,267	Tuckpoint, waterproof & clean.
	340	Exterior Windows (B)	04-28-2005	04-18-2007	2	100%	$5.75	$107,008	Replace all windows. Origional wood casement windows need urgent 
	replacement. Glass is also single p
System:	Roof System (4)	Totals:	$29,265	$125,059
	961	Covering (B)	04-18-2007	04-18-2007	2	25%	$3.25	$15,121	Wood shingles need replacing
	342	Insulation (C)	04-28-2005	04-18-2007	4	50%	$1.52	$14,144	Additional insulation required for energy conservation.
System:	Finishes (5)	Totals:	$312,136	$848,244
	343	Ceilings (B)	04-28-2005	04-18-2007	2	50%	$9.57	$89,049	Replace cracked and loose plaster ceilings.
	344	Interior Doors/Hardware/Windows (C)	04-28-2005	04-18-2007	2	25%	$7.54	$35,080	Replace worn hinges. Replace hallway doors & transoms for fire rating.
	346	Floor Finishes (D)	04-28-2005	04-18-2007	2	75%	$8.87	$123,803	Replace flooring and carpet-worn out.
	347	Wall Finishes (E)	04-28-2005	04-18-2007	2	50%	$6.90	$64,204	Many areas need paint touch up.
System:	Specialties (6)	Totals:	$43,455	$268,356
	348	Toilet Partitions (A)	04-28-2005	04-18-2007	2	100%	$1.75	$32,568	Replace all partitions.
	963	Signage/Directories (B)	04-18-2007	04-18-2007	3	50%	$1.17	$10,887	Door signs need braille upgrade. No Evac maps.
	Deficiency Detail by Building	FCI Version:  1.1.0
	Priorities 1-6	5/12/2009
	Priorities 1-6	Page 36 of 71

	University of Montana - Facilities Condition Inventory	Priorities	1
	Deficiency Detail by Building	2
	Site:	UM Missoula Main Campus	Area Correction:	1.21	Last Audit Date:	4/18/2007	3
	4
	Building:	Mathematics	Gross Area:	18,610	Sq Ft	Report Renewal Cost:	$1,144,408	5
	Category:	3A	Cost/Sq Ft:	$209.31	Deficiency Ratio:	29.4%	6
	Const. Date:	1903	Replacement Cost:	$3,895,259	7
	Comp.	System
	Entry #	Initial	Last	Unit	Renew	Replace
	Component	Entry	Update	Pri	%	Cost	Cost	Cost	Description
System:	HVAC System (7)	Totals:	$95,469	$437,521
	349	Heating (A)	04-28-2005	04-18-2007	2	50%	$10.26	$95,469	Repair piping & valves on existing radiators & steam lines.
System:	Plumbing System (8)	Totals:	$312,391	$413,700
	352	Fixtures (A)	04-28-2005	04-18-2007	2	75%	$7.56	$105,519	Replace old fixtures, faucets and tank toilets.
	353	Supply Piping (B)	04-28-2005	04-18-2007	2	60%	$8.58	$95,804	Replace old worn out piping.
	354	Waste Piping (C)	04-28-2005	04-18-2007	2	98%	$6.09	$111,068	Replace worn out piping and install new gutters & down spouts.
System:	Electrical System (9)	Totals:	$136,039	$578,213
	356	Lighting (B)	04-28-2005	04-18-2007	5	100%	$7.31	$136,039	Install T8 electronic Ballasts & replace exterior lights.
System:	Safety System (11)	Totals:	$7,788	$258,307
	359	Egress (A)	04-28-2005	04-18-2007	3	5%	$2.77	$2,577	Modify exit stairs hand rails.
	362	Asbestos/Hazardous Material (D)	04-28-2005	04-18-2007	4	100%	$0.28	$5,211	Remove Asbestos from tunnel and building.
	Deficiency Detail by Building	FCI Version:  1.1.0
	Priorities 1-6	5/12/2009
	Priorities 1-6	Page 37 of 71

	University of Montana - Facilities Condition Inventory	Priorities	1
	Deficiency Detail by Building	2
	Site:	UM Missoula Main Campus	Area Correction:	0.98	Last Audit Date:	6/4/2008	3
	4
	Building:	McGill Hall	Gross Area:	67,079	Sq Ft	Report Renewal Cost:	$2,796,683	5
	Category:	4B	Cost/Sq Ft:	$198.40	Deficiency Ratio:	21.0%	6
	Const. Date:	1953	Replacement Cost:	$13,308,474	7
	Comp.	System
	Entry #	Initial	Last	Unit	Renew	Replace
	Component	Entry	Update	Pri	%	Cost	Cost	Cost	Description
System:	Foundations (1)	Totals:	$43,333	$867,331
	1005	Footings/Foundation Walls (A)	06-04-2008	06-04-2008	2	5%	$12.18	$40,851	cracks starting to appear, especially on west side
	1006	Exterior Steps/Retaining Walls (B)	06-04-2008	06-04-2008	2	5%	$0.74	$2,482	cracks in steps, mortar work ended at joints.
System:	Envelope (2)	Totals:	$296,824	$1,184,615
	97	Exterior Windows (B)	04-28-2005	04-28-2005	2	20%	$3.12	$41,857	Replace the windows because of damage/wearout with double paned E 
	glass.
	1007	Exterior Windows (B)	06-04-2008	06-04-2008	4	80%	$3.12	$167,429	single pane and separating from frame.
	124	Exterior Doors/Hatches (C)	06-04-2008	04-28-2005	2	50%	$2.61	$87,538	Doors on South and North still need to be replaced
System:	Floor System (3)	Totals:	$31,896	$914,958
	1009	Floor Structure (A)	06-04-2008	06-04-2008	2	5%	$9.51	$31,896	30%  of west entrance is in poor shape
System:	Roof System (4)	Totals:	$221,361	$560,110
	99	Covering (B)	06-04-2008	04-28-2005	2	75%	$4.40	$221,361	Replace old BUR roof with PDM
System:	Finishes (5)	Totals:	$857,839	$2,593,274
	100	Interior Walls (A)	04-28-2005	04-28-2005	2	5%	$14.75	$49,471	Repair cracks in the walls.
	101	Ceilings (B)	06-04-2008	04-28-2005	2	50%	$7.05	$236,453	Replace worn out ceiling tiles.
	102	Interior Doors/Hardware/Windows (C)	06-04-2008	04-28-2005	3	10%	$1.54	$10,330	Provide 20 minue UL label doors at hallways & change out locks set 
	hardware & glazing correspondingly.
	103	Floor Finishes (D)	06-04-2008	04-28-2005	2	10%	$7.72	$51,785	Replace worn-out old tile, wood & dance floors
	104	Wall Finishes (E)	06-04-2008	04-28-2005	2	100%	$7.60	$509,800	Interior walls really need repainting.
	Deficiency Detail by Building	FCI Version:  1.1.0
	Priorities 1-6	5/12/2009
	Priorities 1-6	Page 38 of 71

	University of Montana - Facilities Condition Inventory	Priorities	1
	Deficiency Detail by Building	2
	Site:	UM Missoula Main Campus	Area Correction:	0.98	Last Audit Date:	6/4/2008	3
	4
	Building:	McGill Hall	Gross Area:	67,079	Sq Ft	Report Renewal Cost:	$2,796,683	5
	Category:	4B	Cost/Sq Ft:	$198.40	Deficiency Ratio:	21.0%	6
	Const. Date:	1953	Replacement Cost:	$13,308,474	7
	Comp.	System
	Entry #	Initial	Last	Unit	Renew	Replace
	Component	Entry	Update	Pri	%	Cost	Cost	Cost	Description
System:	Specialties (6)	Totals:	$36,101	$1,159,796
	105	Toilet Partitions (A)	04-28-2005	04-28-2005	3	20%	$1.80	$24,148	Replace old partitions with new ones--also bring to ADA standards. 
	108	Chalk/Tackboards/Cabinets (D)	04-28-2005	04-28-2005	3	3%	$5.94	$11,953	Replace chalkboards with white boards.
System:	HVAC System (7)	Totals:	$369,304	$2,058,655
	109	Heating (A)	06-04-2008	04-28-2005	2	20%	$13.85	$185,809	Replace UV units & 3 AHVs.
	1011	Ventilating (B)	06-04-2008	06-04-2008	2	15%	$12.69	$127,685	Sections of building have little or no air circulation
	1012	Cooling (C)	06-04-2008	06-04-2008	2	20%	$4.16	$55,810	Half of 2nd floor and now with HHP lab addtion there are more sections 
	that have no cooling
System:	Plumbing System (8)	Totals:	$522,914	$1,867,479
	111	Fixtures (A)	06-04-2008	04-28-2005	2	25%	$11.13	$186,647	Replace faulty/leaking showers.
	112	Supply Piping (B)	06-04-2008	04-28-2005	2	30%	$9.05	$182,119	Replace metal recirculating piping with PVC piping on old supply lines
	113	Waste Piping (C)	06-04-2008	04-28-2005	2	30%	$7.66	$154,148	Solve problems of back-up, plugging up waste pipes.
System:	Electrical System (9)	Totals:	$336,415	$1,210,105
	114	Building Service (A)	04-28-2005	04-28-2005	2	3%	$2.74	$5,514	Replace old meter with new.
	115	Lighting (B)	06-04-2008	04-28-2005	5	50%	$5.69	$190,840	Replace old fixtures with T8 electronic ballasts in offices & classrooms.
	116	Distribution (C)	06-04-2008	04-28-2005	2	30%	$6.96	$140,061	Replace old panels, receptacles and switches.
	Deficiency Detail by Building	FCI Version:  1.1.0
	Priorities 1-6	5/12/2009
	Priorities 1-6	Page 39 of 71

	University of Montana - Facilities Condition Inventory	Priorities	1
	Deficiency Detail by Building	2
	Site:	UM Missoula Main Campus	Area Correction:	0.98	Last Audit Date:	6/4/2008	3
	4
	Building:	McGill Hall	Gross Area:	67,079	Sq Ft	Report Renewal Cost:	$2,796,683	5
	Category:	4B	Cost/Sq Ft:	$198.40	Deficiency Ratio:	21.0%	6
	Const. Date:	1953	Replacement Cost:	$13,308,474	7
	Comp.	System
	Entry #	Initial	Last	Unit	Renew	Replace
	Component	Entry	Update	Pri	%	Cost	Cost	Cost	Description
System:	Safety System (11)	Totals:	$80,696	$627,189
	118	Egress (A)	06-04-2008	04-28-2005	3	30%	$2.24	$45,077	still a few existing corridor walls need to be 1hr rated and stairs need to be 
	in 2hr enclosures.
	1014	Exit/Emergency Lighting/Alarms (C)	06-04-2008	06-04-2008	1	5%	$1.54	$5,165	alarm system still needs fine tuning
	121	Asbestos/Hazardous Material (D)	04-28-2005	04-28-2005	3	100%	$0.23	$15,428	Remove asbestos 8x8 tiles and asbestos piping.
	1016	ADA Accessibility (E)	06-04-2008	06-04-2008	3	10%	$2.24	$15,026	Handrails on NE corner needs work
	Deficiency Detail by Building	FCI Version:  1.1.0
	Priorities 1-6	5/12/2009
	Priorities 1-6	Page 40 of 71

	University of Montana - Facilities Condition Inventory	Priorities	1
	Deficiency Detail by Building	2
	Site:	UM Missoula Main Campus	Area Correction:	1.08	Last Audit Date:	5/11/2006	3
	4
	Building:	Music	Gross Area:	37,180	Sq Ft	Report Renewal Cost:	$2,345,986	5
	Category:	3A	Cost/Sq Ft:	$224.34	Deficiency Ratio:	28.1%	6
	Const. Date:	1953	Replacement Cost:	$8,340,961	7
	Comp.	System
	Entry #	Initial	Last	Unit	Renew	Replace
	Component	Entry	Update	Pri	%	Cost	Cost	Cost	Description
System:	Foundations (1)	Totals:	$21,471	$184,785
	694	Exterior Steps/Retaining Walls (B)	05-11-2006	04-28-2005	2	35%	$1.65	$21,471	Repair, regrout steps at main entrance(SW) and at N entrance. Block, slate 
	rock work on W end-
System:	Envelope (2)	Totals:	$223,823	$606,406
	695	Exterior Windows (B)	05-11-2006	04-28-2005	5	100%	$5.13	$190,733	Replace all single pane with low E
	696	Exterior Doors/Hatches (C)	04-28-2005	04-28-2005	2	100%	$0.89	$33,090	Doors are a continual problem needing frequent repair, parts are difficult 
	to find.
System:	Roof System (4)	Totals:	$168,407	$222,708
	698	Structure (A)	04-28-2005	04-28-2005	2	15%	$1.73	$9,648	East entrance patio roof concrete is cracked and leaking. Covering needs to 
	be removed and structure
	699	Covering (B)	04-28-2005	04-28-2005	2	100%	$2.91	$108,194	Install new single membrane roof covering.
	700	Insulation (C)	04-28-2005	04-28-2005	2	100%	$1.36	$50,565	Add insulation before application of new roof covering.
System:	Finishes (5)	Totals:	$408,014	$1,512,482
	701	Ceilings (B)	05-11-2006	04-28-2005	2	10%	$8.54	$31,752	Replace ceiling tile in basement.
	704	Floor Finishes (D)	05-11-2006	04-28-2005	2	50%	$7.92	$147,233	Wood flooring needs sanding and refininshing. Capeting needs replacing
	705	Wall Finishes (E)	05-11-2006	04-28-2005	2	100%	$6.16	$229,029	Walls and stairwells need paint throughout building. Last painted in 1982.
System:	Specialties (6)	Totals:	$148,813	$478,507
	863	Toilet Partitions (A)	05-11-2006	05-11-2006	2	5%	$1.57	$2,919	Repaint metal partitions.
	706	Chalk/Tackboards/Cabinets (D)	04-28-2005	04-28-2005	2	60%	$6.54	$145,894	Replace all chalkboards and replace with LCS boards.
	Deficiency Detail by Building	FCI Version:  1.1.0
	Priorities 1-6	5/12/2009
	Priorities 1-6	Page 41 of 71

	University of Montana - Facilities Condition Inventory	Priorities	1
	Deficiency Detail by Building	2
	Site:	UM Missoula Main Campus	Area Correction:	1.08	Last Audit Date:	5/11/2006	3
	4
	Building:	Music	Gross Area:	37,180	Sq Ft	Report Renewal Cost:	$2,345,986	5
	Category:	3A	Cost/Sq Ft:	$224.34	Deficiency Ratio:	28.1%	6
	Const. Date:	1953	Replacement Cost:	$8,340,961	7
	Comp.	System
	Entry #	Initial	Last	Unit	Renew	Replace
	Component	Entry	Update	Pri	%	Cost	Cost	Cost	Description
System:	HVAC System (7)	Totals:	$780,036	$780,036
	707	Heating (A)	05-11-2006	04-28-2005	2	100%	$9.16	$340,569	Air handlers need replacement, piping is corroded, pipe insulation is bad, 
	steam heating coils need 
	708	Ventilating (B)	05-11-2006	04-28-2005	2	100%	$1.14	$42,385	Most of ventiliation system has been disabled and needs replacement.
	867	Cooling (C)	05-11-2006	05-11-2006	2	100%	$10.68	$397,082	Whole building needs cooling system.
System:	Plumbing System (8)	Totals:	$123,959	$737,651
	709	Fixtures (A)	05-11-2006	04-28-2005	2	30%	$6.75	$75,290	Need replacement.
	869	Supply Piping (B)	05-11-2006	05-11-2006	2	10%	$7.66	$28,480	Galvanized piping needs to be replaced.
	870	Waste Piping (C)	05-11-2006	05-11-2006	2	10%	$5.43	$20,189	Piping starting to deteriorate and needs to be replaced.
System:	Electrical System (9)	Totals:	$431,010	$1,031,001
	710	Building Service (A)	04-28-2005	04-28-2005	2	5%	$7.25	$13,478	Install new meters.
	711	Lighting (B)	05-11-2006	04-28-2005	5	50%	$6.52	$121,207	New T8 lamps with electronic ballasts.
	712	Distribution (C)	04-28-2005	04-28-2005	2	100%	$7.97	$296,325	Distribution panels, switches & recepticles all need to be replaced.
System:	Safety System (11)	Totals:	$40,453	$460,660
	716	Exit/Emergency Lighting/Alarms (C)	05-11-2006	04-28-2005	3	20%	$4.19	$31,157	Upgrade fire alarm system
	717	Asbestos/Hazardous Material (D)	05-11-2006	04-28-2005	4	50%	$0.25	$4,648	Remove all asbestos insulation and spray ceiling and walls.
	872	Asbestos/Hazardous Material (D)	05-11-2006	05-11-2006	1	50%	$0.25	$4,648	Plumbing pipe chases need to have asbestos abated before repair work is 
	performed.
	Deficiency Detail by Building	FCI Version:  1.1.0
	Priorities 1-6	5/12/2009
	Priorities 1-6	Page 42 of 71

	University of Montana - Facilities Condition Inventory	Priorities	1
	Deficiency Detail by Building	2
	Site:	UM Missoula Main Campus	Area Correction:	1.44	Last Audit Date:	4/28/2005	3
	4
	Building:	Native American Studies	Gross Area:	3,149	Sq Ft	Report Renewal Cost:	$223,058	5
	Category:	3A	Cost/Sq Ft:	$299.12	Deficiency Ratio:	23.7%	6
	Const. Date:	1955	Replacement Cost:	$941,929	7
	Comp.	System
	Entry #	Initial	Last	Unit	Renew	Replace
	Component	Entry	Update	Pri	%	Cost	Cost	Cost	Description
System:	Foundations (1)	Totals:	$12,155	$20,846
	78	Footings/Foundation Walls (A)	04-28-2005	04-28-2005	2	50%	$4.42	$6,959	GROUT & SEAL FOUNDATION
	79	Exterior Steps/Retaining Walls (B)	04-28-2005	04-28-2005	2	75%	$2.20	$5,196	REPLACE FRONT & REAR ENTRANCE STEPS & ADD ADA RAMP
System:	Envelope (2)	Totals:	$24,588	$68,459
	80	Exterior Walls (A)	04-28-2005	04-28-2005	2	10%	$5.79	$1,823	PAINT CRACKED AND CHIPPED WALLS
	81	Exterior Windows (B)	04-28-2005	04-28-2005	2	100%	$6.84	$21,539	REPLACE ALL EXTERIOR WINDOWS.  THEY ARE DAMAGED AND
	 WORN OUT.
	82	Exterior Doors/Hatches (C)	04-28-2005	04-28-2005	2	33%	$1.18	$1,226	REPLACE WORN-OUT BACK ENTRANCE DOOR
System:	Floor System (3)	Totals:	$4,786	$85,023
	83	Stair Treads/Risers (B)	04-28-2005	04-28-2005	2	25%	$6.08	$4,786	REPAIR ALL WORN-OUT STAIR TREADS
System:	Roof System (4)	Totals:	$13,042	$25,161
	84	Covering (B)	04-28-2005	04-28-2005	2	100%	$3.87	$12,187	REPLACE ROOF COVERING & EXTEND ROOF OVER BASEMENT 
	ENTRY
	85	Insulation (C)	04-28-2005	04-28-2005	2	15%	$1.81	$855	ADD MORE INSULATION IN ATTIC
System:	Finishes (5)	Totals:	$1,663	$170,802
	86	Floor Finishes (D)	04-28-2005	04-28-2005	2	5%	$10.56	$1,663	REFINISH HARDWOOD FLOOR
	Deficiency Detail by Building	FCI Version:  1.1.0
	Priorities 1-6	5/12/2009
	Priorities 1-6	Page 43 of 71

	University of Montana - Facilities Condition Inventory	Priorities	1
	Deficiency Detail by Building	2
	Site:	UM Missoula Main Campus	Area Correction:	1.44	Last Audit Date:	4/28/2005	3
	4
	Building:	Native American Studies	Gross Area:	3,149	Sq Ft	Report Renewal Cost:	$223,058	5
	Category:	3A	Cost/Sq Ft:	$299.12	Deficiency Ratio:	23.7%	6
	Const. Date:	1955	Replacement Cost:	$941,929	7
	Comp.	System
	Entry #	Initial	Last	Unit	Renew	Replace
	Component	Entry	Update	Pri	%	Cost	Cost	Cost	Description
System:	Plumbing System (8)	Totals:	$70,537	$83,291
	89	Fixtures (A)	04-28-2005	04-28-2005	2	5%	$9.00	$1,417	REPLACE FIXTURES AND REMODEL FOR ADA.
	764	Fixtures (A)	04-28-2005	04-28-2005	3	50%	$9.00	$14,170	REPLACE FIXTURES AND REMODEL FOR ADA.
	90	Supply Piping (B)	04-28-2005	04-28-2005	2	100%	$10.21	$32,151	REPLACE ALL WORN-OUT SUPPLY PIPING
	91	Waste Piping (C)	04-28-2005	04-28-2005	2	100%	$7.24	$22,799	REPLACE ALL WORN-OUT WASTE PIPING
System:	Electrical System (9)	Totals:	$85,810	$116,450
	92	Building Service (A)	04-28-2005	04-28-2005	2	100%	$9.66	$30,419	REPLACE OLD ELECTRICAL SERVICE.  CURRENT SERVICE IS NOT 
	ADEQUATE
	93	Lighting (B)	04-28-2005	04-28-2005	5	80%	$8.70	$21,917	REPLACE ALL LIGHTS/FIXTURES WITH T8 LAMPS & 
	ELECTRONIC BALLASTS
	94	Distribution (C)	04-28-2005	04-28-2005	2	100%	$10.63	$33,474	COMPLETE DISTRIBUTION CHANGE OUT IS NEEDED.
System:	Safety System (11)	Totals:	$10,477	$52,021
	95	Egress (A)	04-28-2005	04-28-2005	3	50%	$3.30	$5,196	CLOSE IN OPEN STAIRWAYS TO MEET CODES. BACK ENTRANCE 
	STEPS ARE NARROW & STEEP.  BUILDING NEEDS A HAN
	96	Exit/Emergency Lighting/Alarms (C)	04-28-2005	04-28-2005	3	30%	$5.59	$5,281	INSTALL FIRE ALARMS
	Deficiency Detail by Building	FCI Version:  1.1.0
	Priorities 1-6	5/12/2009
	Priorities 1-6	Page 44 of 71

	University of Montana - Facilities Condition Inventory	Priorities	1
	Deficiency Detail by Building	2
	Site:	UM Missoula Main Campus	Area Correction:	1.16	Last Audit Date:	10/11/2006	3
	4
	Building:	Natural Sciences	Gross Area:	23,100	Sq Ft	Report Renewal Cost:	$1,085,863	5
	Category:	4A	Cost/Sq Ft:	$261.44	Deficiency Ratio:	18.0%	6
	Const. Date:	1919	Replacement Cost:	$6,039,264	7
	Comp.	System
	Entry #	Initial	Last	Unit	Renew	Replace
	Component	Entry	Update	Pri	%	Cost	Cost	Cost	Description
System:	Foundations (1)	Totals:	$2,044	$373,989
	393	Exterior Steps/Retaining Walls (B)	04-28-2005	10-11-2006	2	5%	$1.77	$2,044	STEPS NEED REPAIR, GROUT WEST ENTRANCE. Pointing SW end.
System:	Envelope (2)	Totals:	$110,719	$489,489
	394	Exterior Walls (A)	04-28-2005	10-11-2006	2	25%	$8.53	$49,261	TUCKPOINT, CLEAN & SEAL ENTIRE BRICK FACADE. 
	TUCKPOINT/MORTAR JOINTS AT GRANITE BASE. REPAIR 
	CRACKS 
	395	Exterior Windows (B)	04-28-2005	10-11-2006	2	85%	$3.13	$61,458	15  WINDOWS HAVE BEEN REPLACED. 85 ARE WORN OUT ORIG. 
	WOOD FRAME AND NEED TO BE REPLACED.
System:	Floor System (3)	Totals:	$5,660	$373,065
	399	Stair Treads/Risers (B)	04-28-2005	10-11-2006	2	5%	$4.90	$5,660	REPAIR RISERS AT S.E. STAIRS LEADING TO 3RD FLOOR. MORTOR
	 IS FLAKING OFF DIRECTLY BELOW WOOSTER STAI
System:	Roof System (4)	Totals:	$64,911	$246,246
	396	Insulation (C)	04-28-2005	10-11-2006	5	100%	$2.81	$64,911	ADDITIONAL INSULATION IN ATTIC IS NEEDED TO BRING UP 
	TO R36 BLOWN IN.
System:	Finishes (5)	Totals:	$89,767	$1,158,696
	397	Interior Walls (A)	04-28-2005	10-11-2006	2	15%	$19.20	$66,528	SOME CRACKS TO INTERIOR PLASTER NEED REPAIR.
	398	Floor Finishes (D)	04-28-2005	10-11-2006	2	10%	$10.06	$23,239	REPLACE OLD TILE VCT FLOORS WHERE DAMAGED. REPLACE 
	WORN OUT CARPET IN  AUDITORIUM.
	Deficiency Detail by Building	FCI Version:  1.1.0
	Priorities 1-6	5/12/2009
	Priorities 1-6	Page 45 of 71

	University of Montana - Facilities Condition Inventory	Priorities	1
	Deficiency Detail by Building	2
	Site:	UM Missoula Main Campus	Area Correction:	1.16	Last Audit Date:	10/11/2006	3
	4
	Building:	Natural Sciences	Gross Area:	23,100	Sq Ft	Report Renewal Cost:	$1,085,863	5
	Category:	4A	Cost/Sq Ft:	$261.44	Deficiency Ratio:	18.0%	6
	Const. Date:	1919	Replacement Cost:	$6,039,264	7
	Comp.	System
	Entry #	Initial	Last	Unit	Renew	Replace
	Component	Entry	Update	Pri	%	Cost	Cost	Cost	Description
System:	Specialties (6)	Totals:	$103,753	$393,162
	400	Fixed Seating/Risers (C)	04-28-2005	10-11-2006	2	15%	$3.99	$13,825	REPLACE CARPET ON AUDITORIUM RISERS.
	401	Chalk/Tackboards/Cabinets (D)	04-28-2005	10-11-2006	2	10%	$7.03	$16,239	REPLACE GREEN CHALK BOARD IN 307 AND BLACK CHALK 
	BOARD IN 102.
	402	Fume Hoods (E)	04-28-2005	10-11-2006	1	100%	$3.19	$73,689	ALL FUME HOODS ARE OLD AND UNSAFE.
System:	HVAC System (7)	Totals:	$86,856	$427,581
	403	Ventilating (B)	04-28-2005	10-11-2006	2	100%	$3.76	$86,856	BUILDINGS RETURN AIR SYSTEM WAS REMOVED AND NEVER 
	REPLACED. RADIANT HEAT SYSTEM IS FUNCTIONAL BUT IN
System:	Plumbing System (8)	Totals:	$341,776	$651,420
	405	Fixtures (A)	04-28-2005	10-11-2006	2	30%	$10.41	$72,141	MOST OF THE FIXTURES IN THE BUILDING ARE ORIGIONAL AND
	 DIFFICULT TO FIND PARTS FOR.
	406	Supply Piping (B)	04-28-2005	10-11-2006	2	100%	$9.63	$222,453	ENTIRE PLUMBING SYSTEM HAS  EXEEDED LIFE EXPECTANCY. 
	ALSO THERE IS A CROSS CONNECTION SOMEWHERE IN T
	407	Waste Piping (C)	04-28-2005	10-11-2006	2	25%	$8.17	$47,182	WASTE SYSTEM IS CAST IRON AND NEEDS REPLACEMENT.
System:	Electrical System (9)	Totals:	$232,098	$446,754
	408	Building Service (A)	04-28-2005	10-11-2006	2	2%	$3.25	$1,502	MAINTENANCE OF SERVICE AND INSTALL NEW METERS.
	409	Lighting (B)	04-28-2005	10-11-2006	5	75%	$5.99	$103,777	INSTALL ELECTRONIC BALLASTS AND T8 LAMPS. CLASS/LABS 
	ALREADY DONE.
	410	Distribution (C)	04-28-2005	10-11-2006	2	75%	$7.32	$126,819	SYSTEM REQUIRES ALL NEW SECONDARY PANELS,  SWITCHES 
	AND OUTLETS. MOST OF THE WIRING IN THE BUILDING 
	Deficiency Detail by Building	FCI Version:  1.1.0
	Priorities 1-6	5/12/2009
	Priorities 1-6	Page 46 of 71

	University of Montana - Facilities Condition Inventory	Priorities	1
	Deficiency Detail by Building	2
	Site:	UM Missoula Main Campus	Area Correction:	1.16	Last Audit Date:	10/11/2006	3
	4
	Building:	Natural Sciences	Gross Area:	23,100	Sq Ft	Report Renewal Cost:	$1,085,863	5
	Category:	4A	Cost/Sq Ft:	$261.44	Deficiency Ratio:	18.0%	6
	Const. Date:	1919	Replacement Cost:	$6,039,264	7
	Comp.	System
	Entry #	Initial	Last	Unit	Renew	Replace
	Component	Entry	Update	Pri	%	Cost	Cost	Cost	Description
System:	Safety System (11)	Totals:	$48,279	$255,717
	413	Exit/Emergency Lighting/Alarms (C)	04-28-2005	10-11-2006	3	100%	$1.82	$42,042	REPLACE EXISTING REAIOACTIVE EXIT SIGNS W/ BATTERY 
	BACK-UP UNITS. PROVIDE HALLWAY EXIT LIGHTS. 
	414	Asbestos/Hazardous Material (D)	04-28-2005	10-11-2006	4	100%	$0.27	$6,237	ABATE PERIMETER, O-SIDE WALL  STEAM LINE, FLR COUNTERS 
	AND ASBESTOS FLR TILE. Vermiculite
	Deficiency Detail by Building	FCI Version:  1.1.0
	Priorities 1-6	5/12/2009
	Priorities 1-6	Page 47 of 71

	University of Montana - Facilities Condition Inventory	Priorities	1
	Deficiency Detail by Building	2
	Site:	UM Missoula Main Campus	Area Correction:	1.44	Last Audit Date:	10/11/2006	3
	4
	Building:	Natural Sciences Annex	Gross Area:	4,890	Sq Ft	Report Renewal Cost:	$225,108	5
	Category:	4A	Cost/Sq Ft:	$324.55	Deficiency Ratio:	14.2%	6
	Const. Date:	1938	Replacement Cost:	$1,587,050	7
	Comp.	System
	Entry #	Initial	Last	Unit	Renew	Replace
	Component	Entry	Update	Pri	%	Cost	Cost	Cost	Description
System:	Envelope (2)	Totals:	$38,159	$128,656
	284	Exterior Walls (A)	04-28-2005	10-11-2006	2	50%	$10.58	$25,868	TUCKPOINT AND SEAL EXTERIOR BRICK WALLS.
	285	Exterior Windows (B)	04-28-2005	10-11-2006	2	40%	$3.89	$7,609	REPLACE OLD SINGLE PANE  WOOD WINDOWS. HALF OF BLDG 
	CONSISTS OF NEW GREEN HOUSE.  LOWERS PERCENTAGE.
	286	Exterior Doors/Hatches (C)	04-28-2005	10-11-2006	2	25%	$3.83	$4,682	REPLACE OLD EXTERIOR DOOR AT NW ENTRANCE NEAR 
	GREENHOUSE.
System:	Roof System (4)	Totals:	$17,017	$64,695
	287	Insulation (C)	04-28-2005	10-11-2006	5	100%	$3.48	$17,017	INCREASE EXISTING BLOWN-IN IN ATTIC TO R36. INSTALL 
	INSULATED HATCH DOOR. Roof insulated
System:	Finishes (5)	Totals:	$15,590	$304,500
	288	Interior Doors/Hardware/Windows (C)	04-28-2005	10-11-2006	2	5%	$2.26	$553	BLINDS IN 106B NEED REPLACEMENT.
	289	Wall Finishes (E)	04-28-2005	10-11-2006	2	25%	$12.30	$15,037	PAINT NEEDED IN 100B, 106A AND 106B.
System:	Specialties (6)	Totals:	$19,364	$103,277
	291	Fume Hoods (E)	04-28-2005	10-11-2006	2	100%	$3.96	$19,364	FUME HOOD IS OLD, MISSING PLEXI SHIELD, DANGEROUS.
System:	HVAC System (7)	Totals:	$13,702	$112,372
	292	Ventilating (B)	04-28-2005	10-11-2006	2	60%	$4.67	$13,702	AIR HANDLERS IN ATTIC HAVE REACHED END OF USEFUL LIFE. 
	GREENHOUSE SECTION OF BUILDING HAS BEEN UPDAT
	Deficiency Detail by Building	FCI Version:  1.1.0
	Priorities 1-6	5/12/2009
	Priorities 1-6	Page 48 of 71

	University of Montana - Facilities Condition Inventory	Priorities	1
	Deficiency Detail by Building	2
	Site:	UM Missoula Main Campus	Area Correction:	1.44	Last Audit Date:	10/11/2006	3
	4
	Building:	Natural Sciences Annex	Gross Area:	4,890	Sq Ft	Report Renewal Cost:	$225,108	5
	Category:	4A	Cost/Sq Ft:	$324.55	Deficiency Ratio:	14.2%	6
	Const. Date:	1938	Replacement Cost:	$1,587,050	7
	Comp.	System
	Entry #	Initial	Last	Unit	Renew	Replace
	Component	Entry	Update	Pri	%	Cost	Cost	Cost	Description
System:	Plumbing System (8)	Totals:	$77,418	$171,199
	293	Fixtures (A)	04-28-2005	10-11-2006	2	25%	$12.92	$15,795	SOME FIXTURES NEED REPLACEMENT.
	294	Supply Piping (B)	04-28-2005	10-11-2006	2	80%	$11.95	$46,748	PLUMBING IS ORIGINAL GALVANIZED OVER 60 YEARS OLD.
	295	Waste Piping (C)	04-28-2005	10-11-2006	2	30%	$10.14	$14,875	SOME WASTE PIPING IS STILL CLAY TILE AND NEEDS 
	REPLACEMENT.
System:	Electrical System (9)	Totals:	$18,380	$117,360
	296	Lighting (B)	04-28-2005	10-11-2006	2	20%	$7.43	$7,267	REPLACE EXISTING INCANDESCANT LIGHTING W/ T8'S.
	297	Distribution (C)	04-28-2005	10-11-2006	2	25%	$9.09	$11,113	DISTRIBUTION PANELS ARE IN POOR CONDITION. SOME 
	BREAKERS SWITCH'S ARE BROKEN(HOT) AND NON-
	FUNCTIONAL
System:	Safety System (11)	Totals:	$25,478	$67,189
	300	Egress (A)	04-28-2005	10-11-2006	3	10%	$3.30	$1,614	INSTALL EGRESS WINDOW - add panic bar or doors
	298	Extinguishing System (B)	04-28-2005	10-11-2006	3	100%	$4.55	$22,250	BUILDING NEEDS AN EXTINGUISHING SYTEM.
	299	Asbestos/Hazardous Material (D)	04-28-2005	10-11-2006	4	100%	$0.33	$1,614	ABATE STEAM PIPES WITHIN BLDG.
	Deficiency Detail by Building	FCI Version:  1.1.0
	Priorities 1-6	5/12/2009
	Priorities 1-6	Page 49 of 71

	University of Montana - Facilities Condition Inventory	Priorities	1
	Deficiency Detail by Building	2
	Site:	UM Missoula Main Campus	Area Correction:	1.21	Last Audit Date:	4/28/2005	3
	4
	Building:	North Corbin Hall	Gross Area:	14,858	Sq Ft	Report Renewal Cost:	$580,623	5
	Category:	3A	Cost/Sq Ft:	$251.34	Deficiency Ratio:	15.5%	6
	Const. Date:	1956	Replacement Cost:	$3,734,410	7
	Comp.	System
	Entry #	Initial	Last	Unit	Renew	Replace
	Component	Entry	Update	Pri	%	Cost	Cost	Cost	Description
System:	Foundations (1)	Totals:	$27,487	$82,759
	180	Exterior Steps/Retaining Walls (B)	04-28-2005	04-28-2005	2	100%	$1.85	$27,487	Replace steps & walls. 
System:	Envelope (2)	Totals:	$92,655	$271,456
	181	Exterior Walls (A)	04-28-2005	04-28-2005	2	10%	$4.86	$7,221	Tuckpoint/clear/seal bricks. 
	182	Exterior Windows (B)	04-28-2005	04-28-2005	2	100%	$5.75	$85,434	Replace all windows. 
System:	Floor System (3)	Totals:	$45,101	$337,128
	184	Floor Structure (A)	04-28-2005	04-28-2005	2	10%	$17.58	$26,120	Repair ramps between Brantly & N. Corbin. 
	185	Stair Treads/Risers (B)	04-28-2005	04-28-2005	2	25%	$5.11	$18,981	Replace stair treads. 
System:	Finishes (5)	Totals:	$198,057	$677,228
	186	Interior Doors/Hardware/Windows (C)	04-28-2005	04-28-2005	2	50%	$7.54	$56,015	Replace all interior doors 3'0" and door handles.  
	187	Floor Finishes (D)	04-28-2005	04-28-2005	2	100%	$8.87	$131,790	Replace all floors. 
	188	Wall Finishes (E)	04-28-2005	04-28-2005	2	10%	$6.90	$10,252	Replace vinyl in hallway (wall covering), 
System:	HVAC System (7)	Totals:	$22,866	$349,312
	189	Heating (A)	04-28-2005	04-28-2005	2	15%	$10.26	$22,866	Replace heating system controls. 
System:	Plumbing System (8)	Totals:	$25,496	$330,293
	190	Supply Piping (B)	04-28-2005	04-28-2005	2	20%	$8.58	$25,496	Remove old supply piping. 
System:	Electrical System (9)	Totals:	$127,868	$461,638
	191	Lighting (B)	04-28-2005	04-28-2005	5	20%	$7.31	$21,722	Replace all lighting and replace w/ electronic ballast and t-8 lamps.
	192	Distribution (C)	04-28-2005	04-28-2005	2	80%	$8.93	$106,146	Install new secondary panels, switchs, outlets. 
	Deficiency Detail by Building	FCI Version:  1.1.0
	Priorities 1-6	5/12/2009
	Priorities 1-6	Page 50 of 71

	University of Montana - Facilities Condition Inventory	Priorities	1
	Deficiency Detail by Building	2
	Site:	UM Missoula Main Campus	Area Correction:	1.21	Last Audit Date:	4/28/2005	3
	4
	Building:	North Corbin Hall	Gross Area:	14,858	Sq Ft	Report Renewal Cost:	$580,623	5
	Category:	3A	Cost/Sq Ft:	$251.34	Deficiency Ratio:	15.5%	6
	Const. Date:	1956	Replacement Cost:	$3,734,410	7
	Comp.	System
	Entry #	Initial	Last	Unit	Renew	Replace
	Component	Entry	Update	Pri	%	Cost	Cost	Cost	Description
System:	Safety System (11)	Totals:	$41,093	$206,229
	194	Exit/Emergency Lighting/Alarms (C)	04-28-2005	04-28-2005	2	33%	$4.69	$22,996	Replace old exit lights.
	195	Exit/Emergency Lighting/Alarms (C)	04-28-2005	04-28-2005	2	20%	$4.69	$13,937	Replace old exit lights.
	196	Asbestos/Hazardous Material (D)	04-28-2005	04-28-2005	3	100%	$0.28	$4,160	remove all asbestos. 
	Deficiency Detail by Building	FCI Version:  1.1.0
	Priorities 1-6	5/12/2009
	Priorities 1-6	Page 51 of 71

	University of Montana - Facilities Condition Inventory	Priorities	1
	Deficiency Detail by Building	2
	Site:	UM Missoula Main Campus	Area Correction:	1.16	Last Audit Date:	5/28/2007	3
	4
	Building:	'OLD' Journalism	Gross Area:	28,916	Sq Ft	Report Renewal Cost:	$1,559,975	5
	Category:	3A	Cost/Sq Ft:	$200.66	Deficiency Ratio:	26.9%	6
	Const. Date:	1937	Replacement Cost:	$5,802,285	7
	Comp.	System
	Entry #	Initial	Last	Unit	Renew	Replace
	Component	Entry	Update	Pri	%	Cost	Cost	Cost	Description
System:	Foundations (1)	Totals:	$7,677	$154,411
	592	Exterior Steps/Retaining Walls (B)	04-28-2005	05-23-2007	2	15%	$1.77	$7,677	South entrance has degraded, need seal repair.
System:	Envelope (2)	Totals:	$211,419	$506,608
	593	Exterior Walls (A)	04-28-2005	05-28-2007	2	25%	$4.66	$33,687	Seal and tuck point.
	594	Exterior Windows (B)	04-28-2005	04-28-2005	2	100%	$5.51	$159,327	All exterior windows are origional wood frame single pane and are nearing
	 the end of their useful li
	595	Exterior Doors/Hatches (C)	04-28-2005	04-28-2005	2	67%	$0.95	$18,405	Replace south & west entrance doors.
System:	Roof System (4)	Totals:	$36,087	$186,219
	596	Covering (B)	04-28-2005	05-28-2007	2	40%	$3.12	$36,087	Buildup portion of roof needs to be replaced.
System:	Finishes (5)	Totals:	$197,829	$1,263,629
	1045	Interior Walls (A)	05-28-2007	05-28-2007	2	10%	$12.18	$35,220	Patch holes on first & settling cracks
	1046	Ceilings (B)	05-28-2007	05-28-2007	2	10%	$9.18	$26,545	Water leakage in carpenter shop
	597	Interior Doors/Hardware/Windows (C)	04-28-2005	05-28-2007	2	5%	$7.23	$10,453	Replace worn out door hinges & locksets & closers.
	598	Floor Finishes (D)	04-28-2005	04-28-2005	2	20%	$8.50	$49,157	Replace old worn out carpet & vct tiles.
	599	Wall Finishes (E)	04-28-2005	05-28-2007	2	40%	$6.61	$76,454	Paint enterior walls that are cracked and worn.
System:	Specialties (6)	Totals:	$51,283	$399,908
	600	Toilet Partitions (A)	04-28-2005	04-28-2005	2	10%	$1.68	$4,858	Repaint metal partitions.
	1048	Fixed Seating/Risers (C)	05-28-2007	05-28-2007	2	5%	$3.99	$5,769	Classroom on 3rd floor needs minor repairs
	601	Chalk/Tackboards/Cabinets (D)	04-28-2005	04-28-2005	4	20%	$7.03	$40,656	Replace chalk boards with LCS boards.
	Deficiency Detail by Building	FCI Version:  1.1.0
	Priorities 1-6	5/12/2009
	Priorities 1-6	Page 52 of 71

	University of Montana - Facilities Condition Inventory	Priorities	1
	Deficiency Detail by Building	2
	Site:	UM Missoula Main Campus	Area Correction:	1.16	Last Audit Date:	5/28/2007	3
	4
	Building:	'OLD' Journalism	Gross Area:	28,916	Sq Ft	Report Renewal Cost:	$1,559,975	5
	Category:	3A	Cost/Sq Ft:	$200.66	Deficiency Ratio:	26.9%	6
	Const. Date:	1937	Replacement Cost:	$5,802,285	7
	Comp.	System
	Entry #	Initial	Last	Unit	Renew	Replace
	Component	Entry	Update	Pri	%	Cost	Cost	Cost	Description
System:	HVAC System (7)	Totals:	$160,050	$651,767
	602	Heating (A)	04-28-2005	04-28-2005	2	50%	$9.84	$142,267	Replace H&V heater coils and cabinets.
	603	Ventilating (B)	04-28-2005	04-28-2005	2	50%	$1.23	$17,783	Replace H&V ventilation blowers.
System:	Plumbing System (8)	Totals:	$479,644	$616,200
	605	Fixtures (A)	04-28-2005	05-28-2007	2	35%	$7.25	$73,374	All plumbing fixtures in the building are 70 years old, are obselete,  have  
	no replacement parts an
	606	Supply Piping (B)	04-28-2005	04-28-2005	2	100%	$8.22	$237,690	All supply water piping is origional galvanized and should be replaced with 
	copper.
	607	Waste Piping (C)	04-28-2005	04-28-2005	2	100%	$5.83	$168,580	All waste piping is origional cast iron and is nearing the end of its useful life.
System:	Electrical System (9)	Totals:	$369,142	$861,408
	608	Lighting (B)	04-28-2005	04-28-2005	5	60%	$7.01	$121,621	Replace fixtures & lights with new T8 's with electronic ballasts. Rms 304, 
	107, 106 and 108 have al
	609	Distribution (C)	04-28-2005	04-28-2005	2	100%	$8.56	$247,521	System is wearing out. Parts are no longer available. Outlets are worn out.  
	Electrical panels & dis
System:	Safety System (11)	Totals:	$46,844	$384,872
	1050	Exit/Emergency Lighting/Alarms (C)	05-28-2007	05-28-2007	2	30%	$4.50	$39,037	Alarm system need to be replaced.
	611	Asbestos/Hazardous Material (D)	04-28-2005	04-28-2005	3	100%	$0.27	$7,807	Encapsulate all asbestos containing materials in building.
	Deficiency Detail by Building	FCI Version:  1.1.0
	Priorities 1-6	5/12/2009
	Priorities 1-6	Page 53 of 71

	University of Montana - Facilities Condition Inventory	Priorities	1
	Deficiency Detail by Building	2
	Site:	UM Missoula Main Campus	Area Correction:	0.98	Last Audit Date:	4/13/2006	3
	4
	Building:	Performing Arts/Radio-T.V.	Gross Area:	71,125	Sq Ft	Report Renewal Cost:	$2,626,747	5
	Category:	3C	Cost/Sq Ft:	$217.16	Deficiency Ratio:	17.0%	6
	Const. Date:	1985	Replacement Cost:	$15,446,216	7
	Comp.	System
	Entry #	Initial	Last	Unit	Renew	Replace
	Component	Entry	Update	Pri	%	Cost	Cost	Cost	Description
System:	Foundations (1)	Totals:	$35,861	$266,719
	834	Footings/Foundation Walls (A)	04-13-2006	04-13-2006	2	2%	$3.01	$4,282	Seam between foundation and sidewalk on east side needs repair
	222	Exterior Steps/Retaining Walls (B)	04-13-2006	04-28-2005	2	50%	$0.74	$26,316	All concrete steps are cracking and pose serious safety hazard.
	223	Exterior Steps/Retaining Walls (B)	04-28-2005	04-28-2005	2	10%	$0.74	$5,263	Replace entry where their are frost heaves in the concrete.
System:	Envelope (2)	Totals:	$122,833	$1,061,185
	836	Exterior Walls (A)	04-13-2006	04-13-2006	2	5%	$3.94	$14,012	Bricks need re-sealing.
	837	Exterior Walls (A)	04-13-2006	04-13-2006	6	10%	$3.94	$28,023	Water from sprinklers has stained brick on several sides.
	224	Exterior Windows (B)	04-13-2006	04-28-2005	2	20%	$5.48	$77,953	Argon gas has leaked out. Overhad windows are stained and need to be 
	cleaned or replaced.
	839	Exterior Doors/Hatches (C)	04-13-2006	04-13-2006	2	5%	$0.80	$2,845	Several exterior doors and frames need to be painted.
System:	Floor System (3)	Totals:	$5,889	$1,307,278
	840	Stair Treads/Risers (B)	04-13-2006	04-13-2006	1	2%	$4.14	$5,889	None of the stair treads have safety stripes or surfaces.
System:	Roof System (4)	Totals:	$164,626	$362,738
	226	Covering (B)	04-13-2006	04-28-2005	2	100%	$2.29	$162,876	Replace damaged/worn out roof with hypalon and new walk pads. All 
	coping needs to be painted.
	842	Insulation (C)	04-13-2006	04-13-2006	2	2%	$1.23	$1,750	Insulation in some areas have been damaged by water leaks and needs to 
	be replaced.
	Deficiency Detail by Building	FCI Version:  1.1.0
	Priorities 1-6	5/12/2009
	Priorities 1-6	Page 54 of 71

	University of Montana - Facilities Condition Inventory	Priorities	1
	Deficiency Detail by Building	2
	Site:	UM Missoula Main Campus	Area Correction:	0.98	Last Audit Date:	4/13/2006	3
	4
	Building:	Performing Arts/Radio-T.V.	Gross Area:	71,125	Sq Ft	Report Renewal Cost:	$2,626,747	5
	Category:	3C	Cost/Sq Ft:	$217.16	Deficiency Ratio:	17.0%	6
	Const. Date:	1985	Replacement Cost:	$15,446,216	7
	Comp.	System
	Entry #	Initial	Last	Unit	Renew	Replace
	Component	Entry	Update	Pri	%	Cost	Cost	Cost	Description
System:	Finishes (5)	Totals:	$388,152	$2,426,074
	843	Interior Walls (A)	04-13-2006	04-13-2006	2	2%	$9.36	$13,315	Several areas need to be repaired and repainted due to condensation 
	damage.
	844	Ceilings (B)	04-13-2006	04-13-2006	2	15%	$7.05	$75,215	Ceiling tiles in several hallways have water stains and need to be replaced.
	227	Interior Doors/Hardware/Windows (C)	04-28-2005	04-28-2005	2	1%	$6.11	$4,346	Install new doors on rest rooms in main lobby area. 
	228	Interior Doors/Hardware/Windows (C)	04-13-2006	04-28-2005	2	5%	$6.11	$21,729	exit door frames in large auditorium are rusting and need to be refinished 
	and repainted
	846	Floor Finishes (D)	04-13-2006	04-13-2006	2	20%	$6.53	$92,889	Carpet need to be replaced in offices and work areas and attempt to match 
	some aisles in auditorium.
	231	Wall Finishes (E)	04-13-2006	04-28-2005	2	50%	$5.08	$180,658	Paint the interior of the building and repair damaged walls.  
System:	HVAC System (7)	Totals:	$1,300,450	$1,969,451
	233	Heating (A)	04-13-2006	04-28-2005	2	60%	$13.85	$591,049	Approx. 040% of heat pumps have been installed.
	234	Ventilating (B)	04-13-2006	04-28-2005	2	100%	$4.16	$295,880	Fresh air inlet pipe size is insufficient for 70K SF building.
	850	Cooling (C)	04-13-2006	04-13-2006	2	60%	$9.69	$413,521	Approx 40% of heat pumps have been replaced.
System:	Plumbing System (8)	Totals:	$43,686	$1,519,941
	851	Fixtures (A)	04-21-2006	04-13-2006	2	2%	$8.17	$11,622	showers in locker rooms need to be rebuilt.
	237	Supply Piping (B)	04-21-2006	04-28-2005	2	3%	$7.72	$16,473	Repace lead pans and roof drains. 
	236	Waste Piping (C)	04-13-2006	04-28-2005	2	4%	$5.48	$15,591	Sewage injectors are getting close to useful life
	Deficiency Detail by Building	FCI Version:  1.1.0
	Priorities 1-6	5/12/2009
	Priorities 1-6	Page 55 of 71

	University of Montana - Facilities Condition Inventory	Priorities	1
	Deficiency Detail by Building	2
	Site:	UM Missoula Main Campus	Area Correction:	0.98	Last Audit Date:	4/13/2006	3
	4
	Building:	Performing Arts/Radio-T.V.	Gross Area:	71,125	Sq Ft	Report Renewal Cost:	$2,626,747	5
	Category:	3C	Cost/Sq Ft:	$217.16	Deficiency Ratio:	17.0%	6
	Const. Date:	1985	Replacement Cost:	$15,446,216	7
	Comp.	System
	Entry #	Initial	Last	Unit	Renew	Replace
	Component	Entry	Update	Pri	%	Cost	Cost	Cost	Description
System:	Electrical System (9)	Totals:	$525,741	$2,120,236
	238	Building Service (A)	04-13-2006	04-28-2005	3	1%	$6.58	$4,680	Replace electrical meters. 
	239	Lighting (B)	04-13-2006	04-28-2005	2	50%	$7.40	$263,162	Stage lighting dimmer system needs to be replaced - can't replace bad 
	parts.
	853	Lighting (B)	04-13-2006	04-13-2006	5	49%	$7.40	$257,899	Replace all incandescent and T-12s
System:	Conveying (10)	Totals:	$2,809	$280,944
	854	Elevator/Lift (A)	04-13-2006	04-13-2006	2	1%	$3.95	$2,809	Doors are rusting on both elevators.
System:	Safety System (11)	Totals:	$36,700	$783,798
	855	Extinguishing System (B)	04-13-2006	04-13-2006	1	5%	$2.72	$9,673	need sprinkler system in theatre and fly loft, a cost study is needed to 
	determine possible costs
	856	Exit/Emergency Lighting/Alarms (C)	04-13-2006	04-13-2006	2	1%	$3.80	$2,703	replace some exit signs
	857	Exit/Emergency Lighting/Alarms (C)	04-13-2006	04-13-2006	3	3%	$3.80	$8,108	Replace some emergency lights
	858	Exit/Emergency Lighting/Alarms (C)	04-13-2006	04-13-2006	3	6%	$3.80	$16,216	Install alarm systems
	Deficiency Detail by Building	FCI Version:  1.1.0
	Priorities 1-6	5/12/2009
	Priorities 1-6	Page 56 of 71

	University of Montana - Facilities Condition Inventory	Priorities	1
	Deficiency Detail by Building	2
	Site:	UM Missoula Main Campus	Area Correction:	0.98	Last Audit Date:	8/22/2008	3
	4
	Building:	Physical Plant	Gross Area:	51,300	Sq Ft	Report Renewal Cost:	$2,269,587	5
	Category:	3B	Cost/Sq Ft:	$214.87	Deficiency Ratio:	20.6%	6
	Const. Date:	1967	Replacement Cost:	$11,023,344	7
	Comp.	System
	Entry #	Initial	Last	Unit	Renew	Replace
	Component	Entry	Update	Pri	%	Cost	Cost	Cost	Description
System:	Envelope (2)	Totals:	$354,380	$765,396
	65	Exterior Walls (A)	04-28-2005	08-22-2008	2	20%	$3.94	$40,424	REPAINT DAMAGED/WORN-OUT EXTERIOR PAINT
	1052	Exterior Windows (B)	08-22-2008	08-22-2008	2	100%	$5.48	$281,124	replace all single pane with low E energy efficient. Better seal office 
	windows
	66	Exterior Doors/Hatches (C)	04-28-2005	08-22-2008	2	80%	$0.80	$32,832	REPLACE WORN-OUT OVERHEAD DOORS
System:	Roof System (4)	Totals:	$88,108	$261,630
	1053	Covering (B)	08-22-2008	08-22-2008	2	75%	$2.29	$88,108	replace old worn out roof covering
System:	Finishes (5)	Totals:	$254,448	$1,749,843
	67	Interior Walls (A)	04-28-2005	04-28-2005	3	15%	$9.36	$72,025	REPLACE CORRIDORS WITH FIRE-RATED EXIT CORRIDORS & 1 
	HR RATED AT OFFICES
	1055	Wall Finishes (E)	08-22-2008	08-22-2008	2	70%	$5.08	$182,423	Paint shops a light color.
System:	HVAC System (7)	Totals:	$909,343	$1,420,497
	70	Heating (A)	04-28-2005	08-22-2008	2	50%	$13.85	$355,252	REPLACE EXISTING WORN-OUT HVAC W/NEW groundwater & 
	STEAM HEATING
	1057	Ventilating (B)	08-22-2008	08-22-2008	2	50%	$4.16	$106,704	air handlers need to be replaced
	1058	Cooling (C)	08-22-2008	08-22-2008	2	90%	$9.69	$447,387	now in east end/west end - 2 condensers - to be replaced
System:	Plumbing System (8)	Totals:	$127,429	$1,075,248
	72	Fixtures (A)	04-28-2005	08-22-2008	3	15%	$7.76	$59,713	UPDATE SHOP TOILET FIXTURES TO MEET ADA STANDARDS
	1060	Supply Piping (B)	08-22-2008	08-22-2008	2	10%	$7.72	$39,604	pipes starting to show wear.
	1061	Waste Piping (C)	08-22-2008	08-22-2008	2	10%	$5.48	$28,112	Piping starting to show wear.
	Deficiency Detail by Building	FCI Version:  1.1.0
	Priorities 1-6	5/12/2009
	Priorities 1-6	Page 57 of 71

	University of Montana - Facilities Condition Inventory	Priorities	1
	Deficiency Detail by Building	2
	Site:	UM Missoula Main Campus	Area Correction:	0.98	Last Audit Date:	8/22/2008	3
	4
	Building:	Physical Plant	Gross Area:	51,300	Sq Ft	Report Renewal Cost:	$2,269,587	5
	Category:	3B	Cost/Sq Ft:	$214.87	Deficiency Ratio:	20.6%	6
	Const. Date:	1967	Replacement Cost:	$11,023,344	7
	Comp.	System
	Entry #	Initial	Last	Unit	Renew	Replace
	Component	Entry	Update	Pri	%	Cost	Cost	Cost	Description
System:	Electrical System (9)	Totals:	$259,372	$1,410,237
	73	Lighting (B)	04-28-2005	08-22-2008	2	50%	$6.65	$170,572	REPLACE DAMAGED/WORN-OUT LIGHTS AT PAINT BOOTH. And 
	all shops.
	74	Distribution (C)	04-28-2005	04-28-2005	2	10%	$8.13	$41,707	REPLACE WORN-OUT GENERATOR WITH NEW
	1062	Voice/Data (D)	08-22-2008	08-22-2008	3	15%	$6.12	$47,093	Data ports don't work in Carpenter's shop
System:	Safety System (11)	Totals:	$276,507	$576,612
	1064	Extinguishing System (B)	08-22-2008	08-22-2008	1	50%	$2.72	$69,768	Many areas are under safe guarded.
	1065	Exit/Emergency Lighting/Alarms (C)	08-22-2008	08-22-2008	1	100%	$3.80	$194,940	exit/emergency lighting/alarms DON'T WORK.
	77	Asbestos/Hazardous Material (D)	04-28-2005	04-28-2005	3	100%	$0.23	$11,799	REPLACE EXISTING SAWDUST COLLECTION AT THE SHOPS TO 
	MEET CODE
	Deficiency Detail by Building	FCI Version:  1.1.0
	Priorities 1-6	5/12/2009
	Priorities 1-6	Page 58 of 71

	University of Montana - Facilities Condition Inventory	Priorities	1
	Deficiency Detail by Building	2
	Site:	UM Missoula Main Campus	Area Correction:	1.04	Last Audit Date:	1/11/2007	3
	4
	Building:	Schreiber Gymnasium	Gross Area:	43,085	Sq Ft	Report Renewal Cost:	$1,696,435	5
	Category:	3A	Cost/Sq Ft:	$216.03	Deficiency Ratio:	18.2%	6
	Const. Date:	1922	Replacement Cost:	$9,307,653	7
	Comp.	System
	Entry #	Initial	Last	Unit	Renew	Replace
	Component	Entry	Update	Pri	%	Cost	Cost	Cost	Description
System:	Foundations (1)	Totals:	$30,892	$205,946
	534	Footings/Foundation Walls (A)	10-04-2005	12-02-2005	2	15%	$3.19	$20,616	Repair water leaks in foundation walls. Determined that leaks will not 
	damage area.
	535	Exterior Steps/Retaining Walls (B)	10-04-2005	01-11-2007	2	15%	$1.59	$10,276	Repair all steps. Repair around joints.
System:	Envelope (2)	Totals:	$90,078	$676,435
	536	Exterior Walls (A)	10-04-2005	01-11-2007	2	10%	$4.18	$18,010	Tuckpoint brick walls & repair damaged terra-cotta and seal exterior.
	537	Exterior Windows (B)	10-04-2005	12-02-2005	2	33%	$4.94	$70,237	Repaint steel windows, repair lead putty to glazing, repair grout & caulk 
	where windows meets brick.
	538	Exterior Doors/Hatches (C)	04-28-2005	01-11-2007	2	5%	$0.85	$1,831	SE of corner damaged doors to pool annex of bldg needs repair
System:	Floor System (3)	Totals:	$32,551	$840,158
	929	Floor Structure (A)	01-11-2007	01-11-2007	2	5%	$15.11	$32,551	entry area main floor has settling occurring.
System:	Roof System (4)	Totals:	$14,110	$248,600
	930	Insulation (C)	01-11-2007	01-11-2007	5	25%	$1.31	$14,110	more insulation is needed in attic area in annex (south of main structure).
System:	Finishes (5)	Totals:	$101,788	$1,688,070
	539	Interior Walls (A)	10-04-2005	01-11-2007	2	10%	$10.92	$47,049	Settling cracks in pool bathrm and plaster walls in various rooms.
	541	Floor Finishes (D)	04-28-2005	04-28-2005	2	5%	$7.62	$16,415	Replace worn carpet & vinyl in offices.
	542	Wall Finishes (E)	04-28-2005	01-11-2007	2	15%	$5.93	$38,324	Patch & paint. Pealing still from previous floor flooding
	Deficiency Detail by Building	FCI Version:  1.1.0
	Priorities 1-6	5/12/2009
	Priorities 1-6	Page 59 of 71

	University of Montana - Facilities Condition Inventory	Priorities	1
	Deficiency Detail by Building	2
	Site:	UM Missoula Main Campus	Area Correction:	1.04	Last Audit Date:	1/11/2007	3
	4
	Building:	Schreiber Gymnasium	Gross Area:	43,085	Sq Ft	Report Renewal Cost:	$1,696,435	5
	Category:	3A	Cost/Sq Ft:	$216.03	Deficiency Ratio:	18.2%	6
	Const. Date:	1922	Replacement Cost:	$9,307,653	7
	Comp.	System
	Entry #	Initial	Last	Unit	Renew	Replace
	Component	Entry	Update	Pri	%	Cost	Cost	Cost	Description
System:	Specialties (6)	Totals:	$30,397	$534,254
	543	Toilet Partitions (A)	04-28-2005	04-28-2005	2	5%	$1.51	$3,253	Replace mens partition.
	932	Chalk/Tackboards/Cabinets (D)	01-11-2007	01-11-2007	6	10%	$6.30	$27,144	blackboard in room 303 needs to be replaced.
System:	HVAC System (7)	Totals:	$237,399	$870,748
	810	Heating (A)	10-04-2005	01-11-2007	2	50%	$8.82	$190,005	Cast iron radiators are at the end of useful life. Parts not avail.
	811	Ventilating (B)	10-04-2005	10-04-2005	2	100%	$1.10	$47,394	Vent louvers were covered by new roofing. Showers have no ventilation, 
	Air handlers are failing.
System:	Plumbing System (8)	Totals:	$459,416	$822,924
	545	Fixtures (A)	10-04-2005	01-11-2007	2	30%	$6.50	$84,016	Replace fixtures at end of useful life.
	546	Supply Piping (B)	10-04-2005	01-11-2007	2	65%	$7.37	$206,399	Supply piping is galvanized and near end of useful life.
	547	Waste Piping (C)	10-04-2005	01-11-2007	2	75%	$5.23	$169,001	Waste piping is 80 year old cast.
System:	Electrical System (9)	Totals:	$584,922	$1,150,800
	548	Lighting (B)	10-04-2005	10-04-2005	5	100%	$6.28	$270,574	Replace ballasts with electronics and lamps with T8's.
	942	Distribution (C)	01-11-2007	01-11-2007	2	95%	$7.68	$314,348	secondary is old and needs to be replaced
System:	Safety System (11)	Totals:	$114,882	$514,004
	551	Exit/Emergency Lighting/Alarms (C)	10-04-2005	10-04-2005	3	66%	$4.04	$114,882	Install new exit signs & emergency lighting.
	Deficiency Detail by Building	FCI Version:  1.1.0
	Priorities 1-6	5/12/2009
	Priorities 1-6	Page 60 of 71

	University of Montana - Facilities Condition Inventory	Priorities	1
	Deficiency Detail by Building	2
	Site:	UM Missoula Main Campus	Area Correction:	0.96	Last Audit Date:	3/1/2006	3
	4
	Building:	Science Complex (Clapp Bldg)	Gross Area:	99,726	Sq Ft	Report Renewal Cost:	$6,592,647	5
	Category:	4B	Cost/Sq Ft:	$238.23	Deficiency Ratio:	27.7%	6
	Const. Date:	1971	Replacement Cost:	$23,758,722	7
	Comp.	System
	Entry #	Initial	Last	Unit	Renew	Replace
	Component	Entry	Update	Pri	%	Cost	Cost	Cost	Description
System:	Foundations (1)	Totals:	$5,096	$1,262,531
	739	Exterior Steps/Retaining Walls (B)	04-28-2005	03-01-2006	2	7%	$0.73	$5,096	Cracked concrete pavers @ NE corner & South end of Breezeway.  
	Grouting needed.
System:	Envelope (2)	Totals:	$493,344	$1,725,260
	740	Exterior Walls (A)	04-28-2005	03-01-2006	2	20%	$7.06	$140,813	Repaint base columns & arches. Pressure wash decorative concrete 
	columns and seal.  Breeze way panel
	741	Exterior Windows (B)	04-28-2005	03-01-2006	5	95%	$3.05	$288,956	Replace all single pane windows with energy efficient two pane lowe-E. 
	742	Exterior Doors/Hatches (C)	04-28-2005	03-01-2006	2	25%	$2.55	$63,575	Replace all aluminum doors due to worn hardware etc.  Replace wx 
	stripping on all wooden doors
System:	Floor System (3)	Totals:	$40,389	$1,332,339
	820	Stair Treads/Risers (B)	03-01-2006	03-01-2006	2	10%	$4.05	$40,389	No slip strips are worn out and need to be replace in all stairways.
System:	Roof System (4)	Totals:	$665,820	$815,759
	821	Structure (A)	03-01-2006	03-01-2006	2	3%	$1.55	$4,637	repair areas where water has leaked thru roof seal and rotted any wooden 
	members
	822	Covering (B)	03-01-2006	03-01-2006	2	100%	$4.31	$429,819	material has deteriorated such that 100% replacement is necessary
	823	Insulation (C)	03-01-2006	03-01-2006	2	100%	$2.32	$231,364	Insulation has been exposed to water leakage and all needs to be replaced.
	Deficiency Detail by Building	FCI Version:  1.1.0
	Priorities 1-6	5/12/2009
	Priorities 1-6	Page 61 of 71

	University of Montana - Facilities Condition Inventory	Priorities	1
	Deficiency Detail by Building	2
	Site:	UM Missoula Main Campus	Area Correction:	0.96	Last Audit Date:	3/1/2006	3
	4
	Building:	Science Complex (Clapp Bldg)	Gross Area:	99,726	Sq Ft	Report Renewal Cost:	$6,592,647	5
	Category:	4B	Cost/Sq Ft:	$238.23	Deficiency Ratio:	27.7%	6
	Const. Date:	1971	Replacement Cost:	$23,758,722	7
	Comp.	System
	Entry #	Initial	Last	Unit	Renew	Replace
	Component	Entry	Update	Pri	%	Cost	Cost	Cost	Description
System:	Finishes (5)	Totals:	$2,033,584	$3,776,624
	743	Interior Walls (A)	04-28-2005	03-01-2006	2	10%	$14.45	$144,104	Patch or replace sheetrock in places where there has been water damage.
	745	Ceilings (B)	04-28-2005	03-01-2006	2	80%	$6.90	$550,488	Ceiling tile throughout building is water damaged and warped and stained.
	746	Interior Doors/Hardware/Windows (C)	04-28-2005	03-01-2006	2	60%	$1.51	$90,352	Replace approximatley 30% of bldgs interior door hardware and 70% of 
	the bldgs blinds and drapes
	744	Floor Finishes (D)	04-28-2005	03-01-2006	2	72%	$7.56	$542,829	Replace all flooring for NASF, not in hallways, bathrooms and stairwells.
	747	Wall Finishes (E)	04-28-2005	03-01-2006	2	95%	$7.45	$705,811	Repint hallway wall fabric, repaint all classrooms/offices & doors & trim.
System:	Specialties (6)	Totals:	$563,852	$1,688,361
	748	Toilet Partitions (A)	04-28-2005	03-01-2006	2	5%	$1.77	$8,826	Some partitions are old & worn out.
	825	Signage/Directories (B)	03-01-2006	03-01-2006	6	30%	$0.93	$27,824	No directional signs should be erected at appropriate entrance locations. 
	Name and Off directories
	749	Fixed Seating/Risers (C)	04-28-2005	03-01-2006	2	90%	$3.67	$329,395	Classroom tablet arms are breaking-poor design. Tables in some of the labs
	 need to be repaired
	750	Chalk/Tackboards/Cabinets (D)	04-28-2005	03-01-2006	2	30%	$5.82	$174,122	Many classrooms/labs still have blackboards that need replacement with 
	LCS boards.
	826	Fume Hoods (E)	03-01-2006	03-01-2006	2	5%	$4.75	$23,685	[laura will supply]
	Deficiency Detail by Building	FCI Version:  1.1.0
	Priorities 1-6	5/12/2009
	Priorities 1-6	Page 62 of 71

	University of Montana - Facilities Condition Inventory	Priorities	1
	Deficiency Detail by Building	2
	Site:	UM Missoula Main Campus	Area Correction:	0.96	Last Audit Date:	3/1/2006	3
	4
	Building:	Science Complex (Clapp Bldg)	Gross Area:	99,726	Sq Ft	Report Renewal Cost:	$6,592,647	5
	Category:	4B	Cost/Sq Ft:	$238.23	Deficiency Ratio:	27.7%	6
	Const. Date:	1971	Replacement Cost:	$23,758,722	7
	Comp.	System
	Entry #	Initial	Last	Unit	Renew	Replace
	Component	Entry	Update	Pri	%	Cost	Cost	Cost	Description
System:	HVAC System (7)	Totals:	$899,328	$2,998,761
	751	Heating (A)	04-28-2005	03-01-2006	2	30%	$13.56	$405,685	Center HVAC will be totally replaced, perimeter fan coils need to be 
	replaced. (186 units total)
	752	Ventilating (B)	04-28-2005	03-01-2006	2	30%	$12.43	$371,878	Center HVAC will be totally replaced, perimeter fan coils need to be 
	replaced.
	753	Cooling (C)	04-28-2005	03-01-2006	2	30%	$4.07	$121,765	Center HVAC will be totally replaced, [Comment here about ground 
	source water cooled?]
System:	Plumbing System (8)	Totals:	$604,569	$2,719,528
	754	Fixtures (A)	04-28-2005	03-01-2006	2	15%	$10.91	$163,202	Existing terrazo sinks/lavs are worn out. Many faucets are corroded  and 
	nearing end of useful life.
	755	Supply Piping (B)	04-28-2005	03-01-2006	2	33%	$8.86	$291,579	recirc line for hot water, some cold water and DI lines need to be replaced.
	756	Waste Piping (C)	04-28-2005	03-01-2006	2	20%	$7.51	$149,788	Waste piping has been failing in places. copper portion of main line needs 
	to be replaced.
System:	Electrical System (9)	Totals:	$855,350	$1,762,158
	829	Building Service (A)	03-01-2006	03-01-2006	3	10%	$2.69	$26,826	[need some comments here.]
	757	Lighting (B)	04-28-2005	03-01-2006	5	90%	$5.58	$500,824	Replace all exterior soffit lighting.  Interior lighting to be switched to T-8s 
	where poss.
	759	Lighting (B)	04-28-2005	04-28-2005	2	10%	$5.58	$55,647	Replace all exterior soffit lighting.
	758	Distribution (C)	04-28-2005	03-01-2006	2	40%	$6.82	$272,053	Replace approx. half of the secondary panels damaged by acid fumes.
System:	Conveying (10)	Totals:	$192,970	$385,940
	760	Elevator/Lift (A)	04-28-2005	03-01-2006	3	50%	$3.87	$192,970	Elevator needs flooring and controls are not compliant with ADA. Bent 
	Shaft leaks.
	Deficiency Detail by Building	FCI Version:  1.1.0
	Priorities 1-6	5/12/2009
	Priorities 1-6	Page 63 of 71

	University of Montana - Facilities Condition Inventory	Priorities	1
	Deficiency Detail by Building	2
	Site:	UM Missoula Main Campus	Area Correction:	0.96	Last Audit Date:	3/1/2006	3
	4
	Building:	Science Complex (Clapp Bldg)	Gross Area:	99,726	Sq Ft	Report Renewal Cost:	$6,592,647	5
	Category:	4B	Cost/Sq Ft:	$238.23	Deficiency Ratio:	27.7%	6
	Const. Date:	1971	Replacement Cost:	$23,758,722	7
	Comp.	System
	Entry #	Initial	Last	Unit	Renew	Replace
	Component	Entry	Update	Pri	%	Cost	Cost	Cost	Description
System:	Safety System (11)	Totals:	$238,345	$913,490
	831	Egress (A)	03-01-2006	03-01-2006	3	5%	$2.20	$10,970	All exit doors need push bars for ADA compliance.
	761	Exit/Emergency Lighting/Alarms (C)	04-28-2005	03-01-2006	2	100%	$1.51	$150,586	Emergency lighting system has no battery backup or emergency power 
	generator. If the power goes out,
	762	Asbestos/Hazardous Material (D)	04-28-2005	04-28-2005	2	100%	$0.22	$21,940	Remove all asbestos in return air plenum and fire safety sprayed on 
	material on steel beams. Noted s
	832	ADA Accessibility (E)	03-01-2006	03-01-2006	3	25%	$2.20	$54,849	Handrails need  to be replaced in all hallways - s/b 4".
	Deficiency Detail by Building	FCI Version:  1.1.0
	Priorities 1-6	5/12/2009
	Priorities 1-6	Page 64 of 71

	University of Montana - Facilities Condition Inventory	Priorities	1
	Deficiency Detail by Building	2
	Site:	UM Missoula Main Campus	Area Correction:	0.93	Last Audit Date:	4/28/2005	3
	4
	Building:	Skaggs Building	Gross Area:	179,775	Sq Ft	Report Renewal Cost:	$2,511,944	5
	Category:	4B	Cost/Sq Ft:	$188.28	Deficiency Ratio:	7.4%	6
	Const. Date:	1979	Replacement Cost:	$33,848,037	7
	Comp.	System
	Entry #	Initial	Last	Unit	Renew	Replace
	Component	Entry	Update	Pri	%	Cost	Cost	Cost	Description
System:	Envelope (2)	Totals:	$61,483	$3,013,029
	139	Exterior Walls (A)	04-28-2005	04-28-2005	2	5%	$6.84	$61,483	Clean & seal exterior brick walls.
System:	Floor System (3)	Totals:	$16,216	$2,328,086
	141	Floor Structure (A)	04-28-2005	04-28-2005	2	1%	$9.02	$16,216	The floors in the penthouse and at the south entrance are cracked and need 
	to be repaired. 
System:	Roof System (4)	Totals:	$751,460	$1,423,818
	140	Covering (B)	04-28-2005	04-28-2005	2	100%	$4.18	$751,460	The entire roof covering needs to be replaced. 
System:	Finishes (5)	Totals:	$1,429,751	$6,595,945
	143	Floor Finishes (D)	04-28-2005	04-28-2005	2	10%	$7.33	$131,775	The carpet is worn and torn in various areas of the building.  Replace with 
	new carpet. 
	144	Wall Finishes (E)	04-28-2005	04-28-2005	2	100%	$7.22	$1,297,976	Paint the entire interior of the building. 
System:	Electrical System (9)	Totals:	$246,292	$3,077,748
	147	Building Service (A)	04-28-2005	04-28-2005	2	1%	$2.60	$4,674	Replace the power meter.  Currently, only half the power meter works. 
	148	Lighting (B)	04-28-2005	04-28-2005	5	20%	$5.40	$194,157	Replace ballasts with electronic ballasts and T8 lights. 
	149	Distribution (C)	04-28-2005	04-28-2005	2	4%	$6.60	$47,461	PM motor control systems. 
System:	Conveying (10)	Totals:	$6,742	$674,156
	150	Elevator/Lift (A)	04-28-2005	04-28-2005	3	1%	$3.75	$6,742	Install ADA phone and audible/visual indicator lights in the elevator. 
	Deficiency Detail by Building	FCI Version:  1.1.0
	Priorities 1-6	5/12/2009
	Priorities 1-6	Page 65 of 71

	University of Montana - Facilities Condition Inventory	Priorities	1
	Deficiency Detail by Building	2
	Site:	UM Missoula Main Campus	Area Correction:	0.96	Last Audit Date:	11/8/2006	3
	4
	Building:	Social Science	Gross Area:	95,246	Sq Ft	Report Renewal Cost:	$2,049,255	5
	Category:	3A	Cost/Sq Ft:	$199.41	Deficiency Ratio:	10.8%	6
	Const. Date:	1923	Replacement Cost:	$18,993,005	7
	Comp.	System
	Entry #	Initial	Last	Unit	Renew	Replace
	Component	Entry	Update	Pri	%	Cost	Cost	Cost	Description
System:	Foundations (1)	Totals:	$21,002	$420,987
	415	Exterior Steps/Retaining Walls (B)	04-28-2005	11-08-2006	2	15%	$1.47	$21,002	Hand rails needed on front steps. Regrout south & west.
System:	Envelope (2)	Totals:	$475,277	$1,381,067
	417	Exterior Walls (A)	04-28-2005	11-08-2006	2	5%	$3.86	$18,382	Clean, tuck point and waterproof walls. Paint trim.
	418	Exterior Windows (B)	04-28-2005	11-08-2006	5	90%	$4.56	$390,890	All windows are single pane.
	923	Exterior Windows (B)	11-08-2006	11-08-2006	2	10%	$4.56	$43,432	Caulk trim.
	419	Exterior Doors/Hatches (C)	04-28-2005	11-08-2006	2	30%	$0.79	$22,573	add brass coverings on doors Front, East & West.
System:	Roof System (4)	Totals:	$182,015	$507,661
	420	Covering (B)	04-28-2005	11-08-2006	2	60%	$2.58	$147,441	Replace North additionwith TPT roof system. Tin roof is rusting, Tile is 
	chipping
	421	Insulation (C)	04-28-2005	11-08-2006	2	30%	$1.21	$34,574	Install additional insulation to North wing roof and some blown-in to South 
	attic.
System:	Finishes (5)	Totals:	$788,589	$3,444,095
	422	Ceilings (B)	04-28-2005	11-08-2006	2	20%	$7.59	$144,583	Replace ceiling tile.
	426	Floor Finishes (D)	04-28-2005	11-08-2006	2	30%	$7.04	$201,160	Replace some Terrazo, carpet, new tile in hallway
	427	Wall Finishes (E)	04-28-2005	11-08-2006	2	85%	$5.47	$442,846	Complete interior paint and install corner guards in offices and classrooms
System:	Specialties (6)	Totals:	$11,087	$1,089,614
	429	Chalk/Tackboards/Cabinets (D)	04-28-2005	11-08-2006	3	2%	$5.82	$11,087	Replace chalkboards with LCS boards.
	Deficiency Detail by Building	FCI Version:  1.1.0
	Priorities 1-6	5/12/2009
	Priorities 1-6	Page 66 of 71

	University of Montana - Facilities Condition Inventory	Priorities	1
	Deficiency Detail by Building	2
	Site:	UM Missoula Main Campus	Area Correction:	0.96	Last Audit Date:	11/8/2006	3
	4
	Building:	Social Science	Gross Area:	95,246	Sq Ft	Report Renewal Cost:	$2,049,255	5
	Category:	3A	Cost/Sq Ft:	$199.41	Deficiency Ratio:	10.8%	6
	Const. Date:	1923	Replacement Cost:	$18,993,005	7
	Comp.	System
	Entry #	Initial	Last	Unit	Renew	Replace
	Component	Entry	Update	Pri	%	Cost	Cost	Cost	Description
System:	HVAC System (7)	Totals:	$203,541	$1,776,338
	430	Heating (A)	04-28-2005	11-08-2006	2	25%	$8.14	$193,826	Replace worn out valves & traps, steam screw, all herman-nelson ht 
	pumps. condesnate pumps req'd.
	431	Ventilating (B)	04-28-2005	11-08-2006	2	10%	$1.02	$9,715	Replace fans on existing classroom exhaust fan units.
System:	Plumbing System (8)	Totals:	$46,004	$1,680,139
	434	Waste Piping (C)	04-28-2005	11-08-2006	2	10%	$4.83	$46,004	Replace all gutters and downspouts.
System:	Electrical System (9)	Totals:	$229,923	$2,347,814
	435	Building Service (A)	04-28-2005	11-08-2006	2	10%	$6.44	$61,338	Meter replacement.
	436	Distribution (C)	04-28-2005	11-08-2006	2	25%	$7.08	$168,585	Replace secondary electrical systems, switchs, outlets, maintenance & 
	service motor controls.
System:	Safety System (11)	Totals:	$91,817	$1,048,658
	438	Exit/Emergency Lighting/Alarms (C)	04-28-2005	11-08-2006	2	20%	$3.72	$70,863	Install new alarm system, Install additional exit lights and emergency 
	generator or other form of ba
	439	Asbestos/Hazardous Material (D)	04-28-2005	11-08-2006	3	100%	$0.22	$20,954	Some floor tile and some fittings. Not a safety issue at this time.
	Deficiency Detail by Building	FCI Version:  1.1.0
	Priorities 1-6	5/12/2009
	Priorities 1-6	Page 67 of 71

	University of Montana - Facilities Condition Inventory	Priorities	1
	Deficiency Detail by Building	2
	Site:	UM Missoula Main Campus	Area Correction:	1.08	Last Audit Date:	7/12/2006	3
	4
	Building:	University (Main) Hall	Gross Area:	32,843	Sq Ft	Report Renewal Cost:	$2,024,141	5
	Category:	3A	Cost/Sq Ft:	$186.82	Deficiency Ratio:	33.0%	6
	Const. Date:	1898	Replacement Cost:	$6,135,729	7
	Comp.	System
	Entry #	Initial	Last	Unit	Renew	Replace
	Component	Entry	Update	Pri	%	Cost	Cost	Cost	Description
System:	Foundations (1)	Totals:	$62,681	$163,230
	302	Footings/Foundation Walls (A)	07-12-2006	04-28-2005	2	55%	$3.32	$59,971	Existing walls are stone rubble w/o any waterproofing or insulation.
	304	Exterior Steps/Retaining Walls (B)	07-12-2006	04-28-2005	2	5%	$1.65	$2,710	All steps need mortar & sealant. Cracked joints from settlement.
System:	Envelope (2)	Totals:	$245,765	$535,669
	305	Exterior Walls (A)	07-12-2006	04-28-2005	2	20%	$4.34	$28,508	Brick & stone needs washing & Tuck-pointing, and sealing.
	306	Exterior Windows (B)	07-12-2006	04-28-2005	2	100%	$5.13	$168,485	Need total replacement. Existing windows are 100 yrs old; wood casement 
	& single pane glass.
	307	Exterior Doors/Hatches (C)	07-12-2006	04-28-2005	2	100%	$0.89	$29,230	Doors are 100 yrs old.
	308	Interior Columns/Beams (D)	07-12-2006	04-28-2005	2	10%	$5.95	$19,542	Walls/Columns/Beams are old & require maintenance.
System:	Floor System (3)	Totals:	$66,507	$665,071
	309	Floor Structure (A)	07-12-2006	04-28-2005	2	10%	$15.69	$51,531	2nd and 3rd floors squeak & joists also.
	310	Stair Treads/Risers (B)	07-12-2006	04-28-2005	2	10%	$4.56	$14,976	Treads/risers need refinishing. Stain and material repair.
System:	Roof System (4)	Totals:	$102,881	$196,730
	311	Structure (A)	07-12-2006	04-28-2005	2	5%	$1.73	$2,841	Repair roof awnings @ east entry. 
	312	Covering (B)	07-12-2006	04-28-2005	2	100%	$2.91	$95,573	Entire roof covering needs replacement, including clock tower turret.
	313	Insulation (C)	07-12-2006	04-28-2005	2	10%	$1.36	$4,467	Add more blown-in insulation.
	Deficiency Detail by Building	FCI Version:  1.1.0
	Priorities 1-6	5/12/2009
	Priorities 1-6	Page 68 of 71

	University of Montana - Facilities Condition Inventory	Priorities	1
	Deficiency Detail by Building	2
	Site:	UM Missoula Main Campus	Area Correction:	1.08	Last Audit Date:	7/12/2006	3
	4
	Building:	University (Main) Hall	Gross Area:	32,843	Sq Ft	Report Renewal Cost:	$2,024,141	5
	Category:	3A	Cost/Sq Ft:	$186.82	Deficiency Ratio:	33.0%	6
	Const. Date:	1898	Replacement Cost:	$6,135,729	7
	Comp.	System
	Entry #	Initial	Last	Unit	Renew	Replace
	Component	Entry	Update	Pri	%	Cost	Cost	Cost	Description
System:	Finishes (5)	Totals:	$388,747	$1,336,053
	314	Interior Walls (A)	07-12-2006	04-28-2005	2	15%	$11.34	$55,866	Old soft bricks on walls need new plaster & work.  Also, same w/ wood lath
	 & plaster walls.
	315	Ceilings (B)	07-12-2006	04-28-2005	2	5%	$8.54	$14,024	ceiling in both north and south stairways is cracking
	316	Interior Doors/Hardware/Windows (C)	07-12-2006	04-28-2005	2	5%	$6.73	$11,052	Existing wood hallway doors grandfathered by code but change out glass 
	panels & transom to fire rate
	317	Floor Finishes (D)	07-12-2006	04-28-2005	2	60%	$7.92	$156,070	Carpet, wood flooring and subflooring is old & needs replacement.
	318	Wall Finishes (E)	07-12-2006	04-28-2005	2	75%	$6.16	$151,735	Needs repaint of old walls, wood panelling, wainscote & acoustical tiles.
System:	Specialties (6)	Totals:	$69,982	$422,689
	320	Toilet Partitions (A)	07-12-2006	04-28-2005	2	80%	$1.57	$41,251	Need total replacement.
	322	Fixed Seating/Risers (C)	07-12-2006	04-28-2005	2	20%	$3.72	$24,435	Damage wear-out to Risers @ third floor.
	323	Chalk/Tackboards/Cabinets (D)	07-12-2006	04-28-2005	2	2%	$6.54	$4,296	Replace chalkbds with LCS boards at southside 3rd floor.
System:	HVAC System (7)	Totals:	$350,763	$689,046
	324	Cooling (C)	07-12-2006	04-28-2005	2	95%	$10.68	$333,225	Old steam heating leaks, some radiaters need replacement. 6" steam piping
	 in basement is worn out
	905	Cooling (C)	07-12-2006	07-12-2006	2	5%	$10.68	$17,538	Window units leak water/moisture into offices.
System:	Plumbing System (8)	Totals:	$424,216	$651,605
	327	Fixtures (A)	07-12-2006	04-28-2005	2	75%	$6.75	$166,268	Toiltet fixtures all old & need replacement.
	328	Supply Piping (B)	07-12-2006	04-28-2005	2	60%	$7.66	$150,946	Existing piping is cast iron &/or galvanized in excess of 104 yrs old, is 
	rusted out and could fail 
	329	Waste Piping (C)	07-12-2006	04-28-2005	2	60%	$5.43	$107,002	As in 8B.  In excess of 104 yrs old.
	Deficiency Detail by Building	FCI Version:  1.1.0
	Priorities 1-6	5/12/2009
	Priorities 1-6	Page 69 of 71

	University of Montana - Facilities Condition Inventory	Priorities	1
	Deficiency Detail by Building	2
	Site:	UM Missoula Main Campus	Area Correction:	1.08	Last Audit Date:	7/12/2006	3
	4
	Building:	University (Main) Hall	Gross Area:	32,843	Sq Ft	Report Renewal Cost:	$2,024,141	5
	Category:	3A	Cost/Sq Ft:	$186.82	Deficiency Ratio:	33.0%	6
	Const. Date:	1898	Replacement Cost:	$6,135,729	7
	Comp.	System
	Entry #	Initial	Last	Unit	Renew	Replace
	Component	Entry	Update	Pri	%	Cost	Cost	Cost	Description
System:	Electrical System (9)	Totals:	$235,582	$910,736
	330	Building Service (A)	07-12-2006	04-28-2005	2	10%	$7.25	$23,811	Upgrade electrical service. Switchgear. Bldg supply is adequate for more 
	panels.
	331	Lighting (B)	07-12-2006	04-28-2005	5	50%	$6.52	$107,068	Upgrade old light fixtures to new energy effecient fixtures.
	907	Distribution (C)	07-12-2006	07-12-2006	1	40%	$7.97	$104,703	Replace panels and upgrade service links.
System:	Safety System (11)	Totals:	$77,017	$406,925
	336	Exit/Emergency Lighting/Alarms (C)	07-12-2006	04-28-2005	3	50%	$4.19	$68,806	No emergency lighting exists. New fire alarm installed. Replace exit lights 
	with battery backups.
	337	Asbestos/Hazardous Material (D)	07-12-2006	04-28-2005	2	100%	$0.25	$8,211	Has asbestos insulation @ steam piping @ basement and asbestos floor tiles
	 @ basement & under carpet
	Deficiency Detail by Building	FCI Version:  1.1.0
	Priorities 1-6	5/12/2009
	Priorities 1-6	Page 70 of 71

	University of Montana - Facilities Condition Inventory	Priorities	1
	Deficiency Detail by Building	2
	Site:	UM Missoula Main Campus	Area Correction:	1.44	Last Audit Date:	4/28/2005	3
	4
	Building:	Urey Lecture Hall	Gross Area:	9,780	Sq Ft	Report Renewal Cost:	$90,972	5
	Category:	3C	Cost/Sq Ft:	$319.09	Deficiency Ratio:	2.9%	6
	Const. Date:	1980	Replacement Cost:	$3,120,798	7
	Comp.	System
	Entry #	Initial	Last	Unit	Renew	Replace
	Component	Entry	Update	Pri	%	Cost	Cost	Cost	Description
System:	Foundations (1)	Totals:	$2,665	$53,986
	245	Exterior Steps/Retaining Walls (B)	04-28-2005	04-28-2005	2	25%	$1.09	$2,665	Replace the east side entry steps. 
System:	Finishes (5)	Totals:	$41,164	$490,271
	246	Floor Finishes (D)	04-28-2005	04-28-2005	2	40%	$9.59	$37,516	Replace the worn out carpet. 
	248	Wall Finishes (E)	04-28-2005	04-28-2005	2	5%	$7.46	$3,648	Replace worn out sound panels. 
System:	HVAC System (7)	Totals:	$7,961	$397,948
	249	Heating (A)	04-28-2005	04-28-2005	4	4%	$20.35	$7,961	Install the Johnson Controls Metasys system in the building. 
System:	Electrical System (9)	Totals:	$25,514	$428,364
	250	Lighting (B)	04-28-2005	04-28-2005	5	24%	$10.87	$25,514	Retrofit light fixtures to flourescent. 
System:	Safety System (11)	Totals:	$13,668	$158,338
	251	Exit/Emergency Lighting/Alarms (C)	04-28-2005	04-28-2005	3	25%	$5.59	$13,668	Upgrade emergency lighting and alarm systems. 
	Deficiency Detail by Building	FCI Version:  1.1.0
	Priorities 1-6	5/12/2009
	Priorities 1-6	Page 71 of 71